| Logo of OPC Foundation, only if this is a joint work. Both logos shall be side by side.. |  | Logo of other organization. Both logos shall be side by side.. | OPC UA Companion Specification |
| --- | --- | --- | --- |
| OPC nnnnn-m |  |  |  |
| OPC UA for Generators Part 1: Generators Draft1.2.0 2026-08-11 Edit the advanced properties to complete the title page. Boxes are used to provide context or guidelines on expected content. Any words or phrases written in red font colour shall be replaced by actual values as appropriate for the companion specification. |  |  |  |

| Specification Type: | Industry Standard Specification | Comments: |  |
| --- | --- | --- | --- |
| Doc-Number | OPC nnnnn-m |  |  |
| Title: | OPC UA for Generators Part 1Generators | Date: | 2026-08-11 |
| Version: | Draft1.2.0 | Software: | MS-Word |
|  |  | Source: | OPC-UA-Generators.docx |
| Author: | <organization> | Status: | Draft |

Template Revisions

| Version | Date | Description |
| --- | --- | --- |
| 1.01.09 | Mar 09, 2020 | M-4665: Link to NodeSet indicates that also ERRATA, Amendments or Revisions are applied. Fixed various styles. |
| 1.01.10 | Apr 29, 2020 | Minor update for the Value attribute (M-5314). |
| 1.01.11 | July 09, 2020 | M-5595: Added better wording and recommendations for NamespaceMetadata as suggested. M-5520: Fixed quotation marks. M-5781: Title "Additional Variable Attributes" misleading. M-5673: Added HasInterface Reference to figure. M-5468: Use of Namespace Index also in Method signatures. M-5789: Clarify use of NamespaceIndex for Profiles or ConformanceUnits in other specifications. |
| 1.01.12 | Nov 16, 2020 | M-5904: BrowseName convention for placeholders. M-6184: The "additional attributes" table shall not be restricted to Value and Description. M-6183: Fix heading names for columns with a browse path. M-6112: Add an example state machine. M-6185: Add new table types to conventions. |
| 1.01.13 | Feb 17, 2021 | M-6302: Updated format for NamespaceMetadata table to make it validatable. M-6317: Added guideline for uncaptioned embedded figures. |
| 1.01.14 | Nov 15, 2021 | M-6264: GeneratesEvent example added. M-7147: Added abbreviated terms used in template. M-6265: No HasSubtype References. M-7265: Added max size for ConformanceUnit description. M-6612: Added definition of capability ID (Annex A.2). M-6150: Extended tables with Conformance Units row. |
| 1.01.15 | Oct 01, 2022 | M-7528: Namespace index also for the “Subtype of” rows. M-8025: Added missing BrowsePath tables for subcomponents. M-6776: Changed the examples for Structure and Union to start with an uppercase character. M-7341: Added extended definition for structures. |
| 1.01.16 | Mar 14, 2023 | M-8638: Updated URL format for schema files (Annex A). Updated URL format for normative references to documents (Clause 2). |
| 1.01.17 | Nov 17, 2023 | M-9196: Conformance Units and Profiles should be in profile database. M-8765: Added URL syntax for individual files. M-9170: Casing of UANodeSet wrong. M-9182: Added reference to IEC specifications. |
| 1.01.18 | Dec 03, 2024 | M-9275: Missing value rank 0. M-9270: Added guidelines to make figures smaller. M-8648: Well-Known BrowseNames. M-9723: Hyperlinks to online reference. |
| 1.01.19 | Jan 21, 2025 | M-9833: Added description on issue reporting to the “Agreement of Use”. |

CONTENTS

1	Scope	11

2	Normative references	12

3	Terms, abbreviated terms and conventions	13

3.1	Overview	13

3.2	Generators terms	13

3.3	Abbreviated terms	13

3.4	Conventions used in this document	14

3.4.1	Conventions for Node descriptions	14

3.4.2	NodeIds and BrowseNames	17

3.4.3	Common Attributes	18

3.4.4	Structures	20

4	General information to Generators and OPC UA	20

4.1	Introduction to Generators	20

4.2	Introduction to OPC Unified Architecture	21

4.2.1	What is OPC UA?	21

4.2.2	Basics of OPC UA	21

4.2.3	Information modelling in OPC UA	22

5	Use cases	26

5.1	General binding guidance	27

5.2	Operational observability	27

5.3	Analytics for predictive maintenance	27

5.4	Analytics for anomaly detection	28

5.5	Energy and load management	28

5.6	Alarm and event distribution	29

5.7	Fleet monitoring and compliance	29

6	Generators information model overview	30

6.1	What is a generator set	30

6.2	Relationship to other companion specifications	30

6.3	Namespaces used by the model	30

6.4	Information model architecture	30

6.5	Composition of a generator set	31

6.6	Design rationale	31

6.7	Organisation of the ObjectTypes	31

6.8	The generator set	32

6.9	The engine and the CAN bus interface	32

6.10	The alternator and its phases	32

6.11	Support subsystems	33

6.12	The controller	33

6.13	Ratings	33

6.14	The operating state machine	33

6.15	Operating modes	34

6.16	Protections and alarms	34

6.17	Transfer switches and paralleling	34

6.18	The generator system	35

6.19	Organisation of the DataTypes	35

6.20	Coverage of the industry	35

7	OPC UA ObjectTypes	36

7.1	GeneratorIdentificationType	36

7.2	GeneratorStateMachineType	36

7.3	J1939DiagnosticInterfaceType	37

7.3.1	ClearPreviouslyActiveDtcs	38

7.4	ExhaustAftertreatmentType	38

7.4.1	InitiateRegeneration	39

7.4.2	InhibitRegeneration	39

7.5	EngineType	39

7.6	AlternatorPhaseType	40

7.7	AlternatorType	40

7.8	FuelSystemType	41

7.9	CoolingSystemType	42

7.10	LubricationSystemType	42

7.11	StartingSystemType	43

7.12	GeneratorControllerType	43

7.13	GeneratorRatingType	44

7.14	GeneratorSetType	44

7.14.1	Start	45

7.14.2	Stop	45

7.14.3	EmergencyStop	46

7.14.4	ResetFaults	46

7.14.5	SetOperatingMode	46

7.14.6	StartTest	46

7.15	TransferSwitchSourceType	47

7.16	AutomaticTransferSwitchType	47

7.16.1	Transfer	48

7.16.2	Retransfer	48

7.16.3	InhibitTransfer	48

7.17	ParallelingControllerType	49

7.17.1	ConnectToBus	49

7.17.2	DisconnectFromBus	50

7.18	GeneratorSystemType	50

8	OPC UA EventTypes	50

8.1	GeneratorProtectionAlarmType	50

9	OPC UA DataTypes	51

9.1	GeneratorOperatingModeEnum	51

9.2	FuelTypeEnum	51

9.3	GeneratorApplicationRatingEnum	52

9.4	ElectricalConnectionEnum	53

9.5	ExcitationTypeEnum	53

9.6	CoolingMethodEnum	53

9.7	AspirationEnum	54

9.8	EmissionsStandardEnum	54

9.9	CanBusStateEnum	55

9.10	TransferSwitchPositionEnum	55

9.11	TransferTransitionTypeEnum	56

9.12	AtsOperatingStateEnum	56

9.13	AlarmSeverityEnum	57

9.14	GeneratorProtectionFunctionEnum	57

9.15	ParallelingSystemStateEnum	60

9.16	AftertreatmentStateEnum	61

9.17	J1939LampStatusEnum	61

9.18	DiagnosticTroubleCodeType	61

9.19	GeneratorProtectionActionEnum	62

9.20	DiagnosticTroubleCodeDataType	62

10	Profiles and conformance units	64

11	Namespaces	64

11.1	Namespace metadata	64

11.2	Handling of OPC UA namespaces	65

Annex A (normative)   Generators namespace and mappings	66

A.1	NodeSet and supplementary files for Generators Information Model	66

A.2	Capability identifier	67

A.3	Node reference	67

Figures

Figure 1 – The scope of OPC UA within an enterprise	22

Figure 2 – A basic Object in an OPC UA Address Space	23

Figure 3 – The relationship between Type Definitions and Instances	24

Figure 4 – Examples of References between Objects	25

Figure 5 – The OPC UA Information Model notation	25

Figure 6 – Graphical notation used by the AddressSpace figures	31

Figure 7 – Composition of a generator set	31

Figure 8 – The Mandatory content of a generator set	32

Figure 9 – The generator operating state machine	33

Tables

Table 1 – Examples of DataTypes	15

Table 2 – Type Definition Table	16

Table 3 – Examples of Other characteristics	16

Table 4 – <some>Type additional References	16

Table 5 – <some>Type additional subcomponents	17

Table 6 – <some>Type Attribute values for child Nodes	17

Table 7 – Common Node Attributes	18

Table 8 – Common Object Attributes	19

Table 9 – Common Variable Attributes	19

Table 10 – Common VariableType Attributes	19

Table 11 – Common Method Attributes	19

Table 12 – Structures without optional fields where none of the fields allow subtypes	20

Table 13 – Structures with optional fields	20

Table 14 – Structures where one or more of the fields allow subtypes	20

Table 15 – Operational observability	27

Table 16 – Analytics for predictive maintenance	28

Table 17 – Analytics for anomaly detection	28

Table 18 – Energy and load management	29

Table 19 – Alarm and event distribution	29

Table 20 – Fleet monitoring and compliance	29

Table 21 – Namespaces used by the model	30

Table 22 – Operating modes	34

Table 23 – Coverage of the industry	35

Table 24 – GeneratorIdentificationType definition	36

Table 25 – GeneratorStateMachineType definition	37

Table 26 – J1939DiagnosticInterfaceType definition	38

Table 27 – ExhaustAftertreatmentType definition	39

Table 28 – InhibitRegeneration Method Arguments	39

Table 29 – InhibitRegeneration Method AddressSpace definition	39

Table 30 – EngineType definition	40

Table 31 – AlternatorPhaseType definition	40

Table 32 – AlternatorType definition	41

Table 33 – FuelSystemType definition	42

Table 34 – CoolingSystemType definition	42

Table 35 – LubricationSystemType definition	43

Table 36 – StartingSystemType definition	43

Table 37 – GeneratorControllerType definition	43

Table 38 – GeneratorRatingType definition	44

Table 39 – GeneratorSetType definition	45

Table 40 – SetOperatingMode Method Arguments	46

Table 41 – SetOperatingMode Method AddressSpace definition	46

Table 42 – StartTest Method Arguments	46

Table 43 – StartTest Method AddressSpace definition	47

Table 44 – TransferSwitchSourceType definition	47

Table 45 – AutomaticTransferSwitchType definition	48

Table 46 – InhibitTransfer Method Arguments	49

Table 47 – InhibitTransfer Method AddressSpace definition	49

Table 48 – ParallelingControllerType definition	49

Table 49 – GeneratorSystemType definition	50

Table 50 – GeneratorProtectionAlarmType definition	51

Table 51 – GeneratorOperatingModeEnum Items	51

Table 52 – GeneratorOperatingModeEnum definition	51

Table 53 – FuelTypeEnum Items	52

Table 54 – FuelTypeEnum definition	52

Table 55 – GeneratorApplicationRatingEnum Items	52

Table 56 – GeneratorApplicationRatingEnum definition	52

Table 57 – ElectricalConnectionEnum Items	53

Table 58 – ElectricalConnectionEnum definition	53

Table 59 – ExcitationTypeEnum Items	53

Table 60 – ExcitationTypeEnum definition	53

Table 61 – CoolingMethodEnum Items	54

Table 62 – CoolingMethodEnum definition	54

Table 63 – AspirationEnum Items	54

Table 64 – AspirationEnum definition	54

Table 65 – EmissionsStandardEnum Items	54

Table 66 – EmissionsStandardEnum definition	55

Table 67 – CanBusStateEnum Items	55

Table 68 – CanBusStateEnum definition	55

Table 69 – TransferSwitchPositionEnum Items	55

Table 70 – TransferSwitchPositionEnum definition	56

Table 71 – TransferTransitionTypeEnum Items	56

Table 72 – TransferTransitionTypeEnum definition	56

Table 73 – AtsOperatingStateEnum Items	56

Table 74 – AtsOperatingStateEnum definition	57

Table 75 – AlarmSeverityEnum Items	57

Table 76 – AlarmSeverityEnum definition	57

Table 77 – GeneratorProtectionFunctionEnum Items	58

Table 78 – GeneratorProtectionFunctionEnum definition	60

Table 79 – ParallelingSystemStateEnum Items	60

Table 80 – ParallelingSystemStateEnum definition	60

Table 81 – AftertreatmentStateEnum Items	61

Table 82 – AftertreatmentStateEnum definition	61

Table 83 – J1939LampStatusEnum Items	61

Table 84 – J1939LampStatusEnum definition	61

Table 85 – DiagnosticTroubleCodeType Items	62

Table 86 – DiagnosticTroubleCodeType definition	62

Table 87 – GeneratorProtectionActionEnum Items	62

Table 88 – GeneratorProtectionActionEnum definition	62

Table 89 – DiagnosticTroubleCodeDataType Items	63

Table 90 – DiagnosticTroubleCodeDataType definition	63

Table 91 – Profiles and conformance units	64

Table 92 – NamespaceMetadata Object for this document	65

Table 93 – Namespaces used in an OpenUSD Server	65

Table 94 – Namespaces used in this document	65

Table 95 – Nodes defined by this document	68

OPC FOUNDATION, OPC Foundation Machinery joint working group

____________

This work (OPC UA Companion Specification Template, by OPC Foundation), identified by OPC Foundation, is free of known copyright restrictions.

<Remove the above Public Domain notice and add a copyright date in the following Agreement of use for the completed specification. If possible (but not legally required), provide attribution to the original author in the following way:

“This specification is a derivative work of the public domain document OPC UA Companion Specification Template, by OPC Foundation”

>

AGREEMENT OF USE

<For joint work, this is the agreement accepted by OPC Foundation and used by most if not all joint companion specifications.

Changes to this agreement will require OPC Foundation review. For non-joint work replace this section with appropriate agreement of use and copyright verbiage.>

COPYRIGHT RESTRICTIONS

- This document is provided "as is" by the OPC Foundation and the OPC Foundation Machinery joint working group.

- Right of use for this specification is restricted to this specification and does not grant rights of use for referred documents.

- Right of use for this specification will be granted without cost.

- This document may be distributed through computer systems, printed or copied as long as the content remains unchanged and the document is not modified.

- OPC Foundation and OPC Foundation Machinery joint working group do not guarantee usability for any purpose and shall not be made liable for any case using the content of this document.

- The user of the document agrees to indemnify OPC Foundation and OPC Foundation Machinery joint working group and their officers, directors and agents harmless from all demands, claims, actions, losses, damages (including damages from personal injuries), costs and expenses (including attorneys' fees) which are in any way related to activities associated with its use of content from this specification.

- The document shall not be used in conjunction with company advertising, shall not be sold or licensed to any party.

- The intellectual property and copyright is solely owned by the OPC Foundation and the OPC Foundation Machinery joint working group.

PATENTS

The attention of adopters is directed to the possibility that compliance with or adoption of OPC or OPC Foundation Machinery joint working group specifications may require use of an invention covered by patent rights. OPC Foundation or OPC Foundation Machinery joint working group shall not be responsible for identifying patents for which a license may be required by any OPC or OPC Foundation Machinery joint working group specification, or for conducting legal inquiries into the legal validity or scope of those patents that are brought to its attention. OPC or OPC Foundation Machinery joint working group specifications are prospective and advisory only. Prospective users are responsible for protecting themselves against liability for infringement of patents.

WARRANTY AND LIABILITY DISCLAIMERS

WHILE THIS PUBLICATION IS BELIEVED TO BE ACCURATE, IT IS PROVIDED "AS IS" AND MAY CONTAIN ERRORS OR MISPRINTS. THE OPC FOUDATION NOR OPC Foundation Machinery joint working group MAKES NO WARRANTY OF ANY KIND, EXPRESSED OR IMPLIED, WITH REGARD TO THIS PUBLICATION, INCLUDING BUT NOT LIMITED TO ANY WARRANTY OF TITLE OR OWNERSHIP, IMPLIED WARRANTY OF MERCHANTABILITY OR WARRANTY OF FITNESS FOR A PARTICULAR PURPOSE OR USE. IN NO EVENT SHALL THE OPC FOUNDATION NOR OPC Foundation Machinery joint working group BE LIABLE FOR ERRORS CONTAINED HEREIN OR FOR DIRECT, INDIRECT, INCIDENTAL, SPECIAL, CONSEQUENTIAL, RELIANCE OR COVER DAMAGES, INCLUDING LOSS OF PROFITS, REVENUE, DATA OR USE, INCURRED BY ANY USER OR ANY THIRD PARTY IN CONNECTION WITH THE FURNISHING, PERFORMANCE, OR USE OF THIS MATERIAL, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGES.

The entire risk as to the quality and performance of software developed using this specification is borne by you.

RESTRICTED RIGHTS LEGEND

This Specification is provided with Restricted Rights. Use, duplication, or disclosure by the U.S. government is subject to restrictions as set forth in (a) this Agreement pursuant to DFARs 227.7202-3(a); (b) subparagraph (c)(1)(i) of the Rights in Technical Data and Computer Software clause at DFARs 252.227-7013; or (c) the Commercial Computer Software Restricted Rights clause at FAR 52.227-19 subdivision (c)(1) and (2), as applicable. Contractor / manufacturer are the OPC Foundation, 16101 N. 82nd Street, Suite 3B, Scottsdale, AZ, 85260-1830

COMPLIANCE

The combination of OPC Foundation Machinery joint working group and OPC Foundation shall at all times be the sole entities that may authorize developers, suppliers and sellers of hardware and software to use certification marks, trademarks, or other special designations to indicate compliance with these materials as specified within this document. Products developed using this specification may claim compliance or conformance with this specification if and only if the software satisfactorily meets the certification requirements set by OPC Foundation Machinery joint working group or the OPC Foundation. Products that do not meet these requirements may claim only that the product was based on this specification and must not claim compliance or conformance with this specification.

Trademarks

Most computer and software brand names have trademarks or registered trademarks. The individual trademarks have not been listed here.

GENERAL PROVISIONS

Should any provision of this Agreement be held to be void, invalid, unenforceable, or illegal by a court, the validity and enforceability of the other provisions shall not be affected thereby.

This Agreement shall be governed by and construed under the laws of Germany.

This Agreement embodies the entire understanding between the parties with respect to, and supersedes any prior understanding or agreement (oral or written) relating to, this specification.

ISSUE REPORTING

If an error or problem is found in this specification, the UaNodeSet, or any associated supplementary files, it should be reported as an issue.

The reporting process can be found here: https://opcfoundation.org/resources/issue-tracking/

The Link to the issue tracking project for this document is here:

https://mantis.opcfoundation.org/set_project.php?project_id=<nnn>&make_default=no

<nnn> is the project_id in Mantis which is created for any document when requested by the working group. Example: https://mantis.opcfoundation.org/set_project.php?project_id=142&make_default=no is the Link for OPC 40001-* (Machinery).

If you have no Mantis Project or do not know the project_id, please send a request to TechnicalDirector@opcfoundation.org.

Release 1.2.0 highlights

<Revision Highlights specify the interesting changes to the previous revision. Such a "Revision Highlights" clause will not exist in the first revision.>

The table below follows the design and process used for the OPC UA specification. All "interesting" changes need to be reported in the problem tracking tool used for the specification. The OPC Foundation uses Mantis and provides it for companion specs as well. If a different problem tracking tool is used, "Mantis" needs to be replaced.

<The two rows in the following table are just examples. Note that the "Mantis IDs" are real hyperlinks – when clicked the reader opens the Mantis page.>

Scope shall specify the type of change. The three options are Errata (corrected something that was wrong), Clarification (make something clearer that was not wrong), and Feature (added new functionality).

The following table includes the Mantis issues resolved with this revision.

| Mantis ID | Scope | Summary | Resolution |
| --- | --- | --- | --- |
| 3165 | Errata | Wrong variable data types in Program example. | Fixed datatypes and replaced Table A.14 by description of the variables. |
| 3521 | Clarification | Modelling rules for states and transitions. | Removed the modelling rules from state and transition objects as they are never created (multiple tables). |

OPC UA FOR GENERATORS

Part 1: Generator sets

# Scope

This specification defines the OPC UA ObjectTypes, VariableTypes, DataTypes, ReferenceTypes and their instances required to represent a generator set as an automation asset and, at the same time, as a machine that is built around a prime‑mover engine exposing a CAN bus / SAE J1939 interface.

The model covers:

- The generator set as a whole (nameplate/identification, ratings, operating state and mode, health, control methods).

- The prime‑mover engine, its telemetry (typically read over CAN/J1939) and its diagnostic trouble codes (DTCs).

- The alternator (generator end), including per‑phase and aggregate electrical measurements.

- Supporting subsystems: fuel, cooling, lubrication, starting/battery, and exhaust aftertreatment.

- The controller / control panel and its remote‑monitoring status.

- Protection and alarm functions (warnings, shutdowns, electrical trips, lockouts).

- Automatic transfer switches (ATS) and paralleling / switchgear for multi‑set power systems.

The model deliberately reuses the OPC UA Devices (DI) and Machinery companion specifications so that generator sets appear as first‑class members of the existing OPC UA machine/asset ecosystem.

NOTE   PROVISIONAL WORKING DRAFT — not normative, not endorsed by the OPC Foundation. The document number, the Mantis project identifier and every NodeId in this document are placeholders; the OPC Foundation assigns the real values.

OPC Foundation

OPC is the interoperability standard for the secure and reliable exchange of data and information in the industrial automation space and in other industries. It is platform independent and ensures the seamless flow of information among devices from multiple vendors. The OPC Foundation is responsible for the development and maintenance of this standard.

OPC UA is a platform independent service-oriented architecture that integrates all the functionality of the individual OPC Classic specifications into one extensible framework. This multi-layered approach accomplishes the original design specification goals of:

- Platform independence: from an embedded microcontroller to cloud-based infrastructure

- Secure: encryption, authentication, authorisation, and auditing

- Extensible: ability to add new features including transports without affecting existing applications

- Comprehensive information modelling capabilities: for defining any model from simple to complex

OPC Foundation Machinery joint working group

# Normative references

The following referenced documents are indispensable for the application of this document. For dated references, only the edition cited applies. For undated references, the latest edition of the referenced document (including any amendments and errata) applies.

NOTE   The OPC UA core specifications are regularly published as IEC 62541.

OPC 10000-1, OPC Unified Architecture - Part 1: Overview and Concepts

http://www.opcfoundation.org/documents/10000-1/

OPC 10000-2, OPC Unified Architecture - Part 2: Security Model

http://www.opcfoundation.org/documents/10000-2/

OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model

http://www.opcfoundation.org/documents/10000-3/

OPC 10000-4, OPC Unified Architecture - Part 4: Services

http://www.opcfoundation.org/documents/10000-4/

OPC 10000-5, OPC Unified Architecture - Part 5: Information Model

http://www.opcfoundation.org/documents/10000-5/

OPC 10000-6, OPC Unified Architecture - Part 6: Mappings

http://www.opcfoundation.org/documents/10000-6/

OPC 10000-7, OPC Unified Architecture - Part 7: Profiles

http://www.opcfoundation.org/documents/10000-7/

OPC 10000-8, OPC Unified Architecture - Part 8: Data Access, which defines AnalogUnitType and the engineering-unit Properties every measured value carries.

http://www.opcfoundation.org/documents/10000-8/

OPC 10000-9, OPC Unified Architecture - Part 9: Alarms and Conditions

http://www.opcfoundation.org/documents/10000-9/

OPC 10000-12, OPC Unified Architecture - Part 12: Discovery and Global Services

http://www.opcfoundation.org/documents/10000-12/

OPC 10000-14, OPC Unified Architecture - Part 14: PubSub

http://www.opcfoundation.org/documents/10000-14/

OPC 10000-16, OPC Unified Architecture - Part 16: State Machines

http://www.opcfoundation.org/documents/10000-16/

OPC 10000-100, OPC Unified Architecture - Part 100: Devices, the DI companion specification whose DeviceType and ComponentType this model derives from.

http://www.opcfoundation.org/documents/10000-100/

OPC 40001-1, OPC UA for Machinery - Part 1: Basic Building Blocks, whose Machines folder makes a generator set discoverable.

http://www.opcfoundation.org/documents/40001-1/

SAE J1939, Serial control and communications heavy duty vehicle network, the CAN bus protocol the engine interface mirrors.

https://www.sae.org/standards/content/j1939/

# Terms, abbreviated terms and conventions

## Overview

## Generators terms

It is assumed that basic concepts of OPC UA information modelling and of Generators are understood in this document. This document uses these concepts to describe the Generators Information Model. For the purposes of this document, the terms and definitions given in OPC 10000-1, OPC 10000-3, OPC 10000-4, OPC 10000-5 and OPC 10000-7, as well as the following, apply.

OPC UA terms and terms defined in this document are italicized in the document.

## Abbreviated terms

GenSet / Generator set

A complete power‑generation unit combining a prime‑mover engine and an alternator with control and support subsystems.

Prime mover

The engine that drives the alternator (diesel, gas, etc.).

Alternator

The AC generator end that converts mechanical power into electrical power.

ATS

Automatic Transfer Switch.

AVR

Automatic Voltage Regulator.

DTC

Diagnostic Trouble Code (SAE J1939 DM1/DM2).

SPN / FMI

Suspect Parameter Number / Failure Mode Identifier (SAE J1939).

ESP / PRP / COP / LTP

ISO 8528 ratings: Emergency Standby / Prime / Continuous / Limited‑Time Power.

DCC

Data‑Center Continuous rating.

PMG

Permanent Magnet Generator (excitation).

## Conventions used in this document

Following are basic conventions that shall be followed for all formal definitions used.

### Conventions for Node descriptions

#### Node definitions

Node definitions are specified using tables (see Table 2).

Attributes are defined by providing the Attribute name and a value, or a description of the value.

References are defined by providing the ReferenceType name, the BrowseName of the TargetNode and its NodeClass.

If the TargetNode is a component of the Node being defined in the table the Attributes of the composed Node are defined in the same row of the table.

The DataType is only specified for Variables; “[<number>]” indicates a single-dimensional array, for multi-dimensional arrays the expression is repeated for each dimension (e.g. [2][3] for a two-dimensional array). For all arrays the ArrayDimensions is set as identified by <number> values. If no <number> is set, the corresponding dimension is set to 0, indicating an unknown size. If no number is provided at all the ArrayDimensions can be omitted. If no brackets are provided, it identifies a scalar DataType and the ValueRank is set to the corresponding value (see OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model). In addition, ArrayDimensions is set to null or is omitted. If it can be Any or ScalarOrOneDimension, the value is put into “{<value>}”, so either “{Any}” or “{ScalarOrOneDimension}” and the ValueRank is set to the corresponding value (see OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model) and the ArrayDimensions is set to null or is omitted. Examples are given in Table 1.

Table 1 – Examples of DataTypes

| Notation | DataType | ValueRank | ArrayDimensions | Description |
| --- | --- | --- | --- | --- |
| 0:Int32 | 0:Int32 | -1 | omitted or null | A scalar Int32. |
| 0:Int32{OneOrMoreDimensions} | 0:Int32 | 0 | omitted or null | The Int32 value is an array with one or more dimensions. |
| 0:Int32[] | 0:Int32 | 1 | omitted or {0} | Single-dimensional array of Int32 with an unknown size. |
| 0:Int32[][] | 0:Int32 | 2 | omitted or {0,0} | Two-dimensional array of Int32 with unknown sizes for both dimensions. |
| 0:Int32[3][] | 0:Int32 | 2 | {3,0} | Two-dimensional array of Int32 with a size of 3 for the first dimension and an unknown size for the second dimension. |
| 0:Int32[5][3] | 0:Int32 | 2 | {5,3} | Two-dimensional array of Int32 with a size of 5 for the first dimension and a size of 3 for the second dimension. |
| 0:Int32{Any} | 0:Int32 | -2 | omitted or null | An Int32 where it is unknown if it is scalar or array with any number of dimensions. |
| 0:Int32{ScalarOrOneDimension} | 0:Int32 | -3 | omitted or null | An Int32 where it is either a single-dimensional array or a scalar. |

The TypeDefinition is specified for Objects and Variables.

The TypeDefinition column specifies a symbolic name for a NodeId, i.e., the specified Node points with a HasTypeDefinition Reference to the corresponding Node.

The ModellingRule of the referenced component is provided by specifying the symbolic name of the rule in the ModellingRule column. In the AddressSpace, the Node shall use a HasModellingRule Reference to point to the corresponding ModellingRule Object.

If the NodeId of a DataType is provided, the symbolic name of the Node representing the DataType shall be used.

Note that if a symbolic name of a different namespace is used, it is prefixed by the NamespaceIndex (see 3.4.2.2).

Nodes of all other NodeClasses cannot be defined in the same table; therefore, only the used ReferenceType, their NodeClass and their BrowseName are specified. A reference to another part of this document points to their definition. Table 2 illustrates the table. If no components are provided, the DataType, TypeDefinition and Other columns can be omitted and only a Comment column is introduced to point to the Node definition.

Each Type Node or well-known Instance Node defined shall have one or more ConformanceUnits defined in 10 that require the Node to be in the AddressSpace.

The relations between Nodes and ConformanceUnits are defined at the end of the tables defining Nodes, one row per ConformanceUnit. The ConformanceUnits are reflected in the Category element for the Node definition in the UANodeSet (see OPC 10000-6, OPC Unified Architecture - Part 6: Mappings).

The list of ConformanceUnits in the UANodeSet allows Servers to optimize resource consumption by using a list of supported ConformanceUnits to select a subset of the Nodes in an Information Model.

When a Node is selected in this way, all dependencies implied by the References are also selected.

Dependencies exist if the Node is the source of HasTypeDefinition, HasInterface, HasAddIn or any HierarchicalReference. Dependencies also exist if the Node is the target of a HasSubtype Reference. For Variables and VariableTypes, the value of the DataType Attribute is a dependency. For DataType Nodes, any DataTypes referenced in the DataTypeDefinition Attribute are also dependencies.

For additional details see OPC 10000-5, OPC Unified Architecture - Part 5: Information Model.

Table 2 – Type Definition Table

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Attribute name | Attribute value. If it is an optional Attribute that is not set “--” is used. |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| ReferenceType name | NodeClass of the target Node. | BrowseName of the target Node. | DataType of the referenced Node, only applicable for Variables. | TypeDefinition of the referenced Node, only applicable for Variables and Objects. | Additional characteristics of the TargetNode such as the ModellingRule or AccessLevel. |
| NOTE Notes referencing footnotes of the table content. |  |  |  |  |  |
| Conformance Units |  |  |  |  |  |
| Name of ConformanceUnit, one row per ConformanceUnit |  |  |  |  |  |

Components of Nodes can be complex that is containing components by themselves. The TypeDefinition, NodeClass and DataType can be derived from the type definitions, and the symbolic name can be created as defined in 3.4.3.1. Therefore, those containing components are not explicitly specified; they are implicitly specified by the type definitions.

The Other column defines additional characteristics of the Node. Examples of characteristics that can appear in this column are show in Table 3.

Table 3 – Examples of Other characteristics

| Name | Short Name | Description |
| --- | --- | --- |
| 0:Mandatory | M | The Node has the Mandatory ModellingRule. |
| 0:Optional | O | The Node has the Optional ModellingRule. |
| 0:MandatoryPlaceholder | MP | The Node has the MandatoryPlaceholder ModellingRule. |
| 0:OptionalPlaceholder | OP | The Node has the OptionalPlaceholder ModellingRule. |
| ReadOnly | RO | The Node AccessLevel has the CurrentRead bit set but not the CurrentWrite bit. |
| ReadWrite | RW | The Node AccessLevel has the CurrentRead and CurrentWrite bits set. |
| WriteOnly | WO | The Node AccessLevel has the CurrentWrite bit set but not the CurrentRead bit. |

If multiple characteristics are defined, they are separated by commas. The name or the short name can be used.

#### Additional References

To provide information about additional References, the format as shown in Table 4 is used.

Table 4 – <some>Type additional References

| SourceBrowsePath | Reference Type | Is Forward | TargetBrowsePath |
| --- | --- | --- | --- |
| SourceBrowsePath is always relative to the TypeDefinition. Multiple elements are defined as separate rows of a nested table. | ReferenceType name | True = forward Reference. | TargetBrowsePath points to another Node, which can be a well-known instance or a TypeDefinition. You can use BrowsePaths here as well, which is either relative to the TypeDefinition or absolute. If absolute, the first entry needs to refer to a type or well-known instance, uniquely identified within a namespace by the BrowseName. |

References can be to any other Node.

#### Additional sub-components

To provide information about sub-components, the format as shown in Table 5 is used.

Table 5 – <some>Type additional subcomponents

| BrowsePath | References | NodeClass | BrowseName | DataType | TypeDefinition | Others |
| --- | --- | --- | --- | --- | --- | --- |
| BrowsePath is always relative to the TypeDefinition. Multiple elements are defined as separate rows of a nested table | NOTE Same as for Table 2 |  |  |  |  |  |

#### Additional Attribute values

The type definition table provides columns to specify the values for required Node Attributes for InstanceDeclarations. To provide information about additional Attributes, the format as shown in Table 6 is used.

Table 6 – <some>Type Attribute values for child Nodes

| BrowsePath | <Attribute name> Attribute |
| --- | --- |
| BrowsePath is always relative to the TypeDefinition. Multiple elements are defined as separate rows of a nested table | The values of attributes are converted to text by adapting the reversible JSON encoding rules defined in OPC 10000-6. If the JSON encoding of a value is a JSON string or a JSON number then that value is entered in the value field. Double quotes are not included. If the DataType includes a NamespaceIndex (QualifiedNames, NodeIds or ExpandedNodeIds) then the notation used for BrowseNames is used. If the value is an Enumeration the name of the enumeration value is entered. If the value is a Structure then a sequence of name and value pairs is entered. Each pair is followed by a newline. The name is followed by a colon. The names are the names of the fields in the DataTypeDefinition. If the value is an array of non-structures then a sequence of values is entered where each value is followed by a newline. If the value is an array of Structures or a Structure with fields that are arrays or with nested Structures then the complete JSON array or JSON object is entered. |

There can be multiple columns to define more than one Attribute.

### NodeIds and BrowseNames

#### NodeIds

The NodeIds of all Nodes described in this standard are only symbolic names. Annex A defines the actual NodeIds.

The symbolic name of each Node defined in this document is its BrowseName, or, when it is part of another Node, the BrowseName of the other Node, a “.”, and the BrowseName of itself. In this case “part of” means that the whole has a HasProperty or HasComponent Reference to its part. Since all Nodes not being part of another Node have a unique name in this document, the symbolic name is unique.

The NamespaceUri for all NodeIds defined in this document is defined in Annex A. The NamespaceIndex for this NamespaceUri is vendor-specific and depends on the position of the NamespaceUri in the server namespace table.

Note that this document not only defines concrete Nodes, but also requires that some Nodes shall be generated, for example one for each Session running on the Server. The NodeIds of those Nodes are Server-specific, including the namespace. But the NamespaceIndex of those Nodes cannot be the NamespaceIndex used for the Nodes defined in this document, because they are not defined by this document but generated by the Server.

#### BrowseNames

The text part of the BrowseNames for all Nodes defined in this document is specified in the tables defining the Nodes. The NamespaceUri for all BrowseNames defined in this document is defined in 11.2.

For InstanceDeclarations of NodeClass Object and Variable that are placeholders (OptionalPlaceholder and MandatoryPlaceholder ModellingRule), the BrowseName and the DisplayName are enclosed in angle brackets (<>) as recommended in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model.

If a BrowseName is not defined by this document, a namespace index prefix is added to the BrowseName (e.g., prefix '0' leading to ‘0:EngineeringUnits’ or prefix '2' leading to ‘2:DeviceRevision’). This is typically necessary if a Property of another specification is overwritten or used in the OPC UA types defined in this document. Table 94 – Namespaces used in this document provides a list of namespaces and their indexes as used in this document.

### Common Attributes

#### General

The Attributes of Nodes, their DataTypes and descriptions are defined in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model. Attributes not marked as optional are mandatory and shall be provided by a Server. The following tables define if the Attribute value is defined by this document or if it is server-specific.

For all Nodes specified in this document, the Attributes named in Table 7 shall be set as specified in the table.

Table 7 – Common Node Attributes

| Attribute | Value |
| --- | --- |
| DisplayName | The DisplayName is a LocalizedText. Each Server shall provide the DisplayName identical to the BrowseName of the Node for the LocaleId “en” unless specified differently in the specification. Whether the Server provides translated names for other LocaleIds is server-specific. |
| Description | Optionally a server-specific description is provided. |
| NodeClass | Shall reflect the NodeClass of the Node. |
| NodeId | The NodeId is described by BrowseNames as defined in 3.4.2.1. |
| WriteMask | Optionally the WriteMask Attribute can be provided. If the WriteMask Attribute is provided, it shall set all non-server-specific Attributes to not writable. For example, the Description Attribute can be set to writable since a Server can provide a server-specific description for the Node. The NodeId shall not be writable, because it is defined for each Node in this document. |
| UserWriteMask | Optionally the UserWriteMask Attribute can be provided. The same rules as for the WriteMask Attribute apply. |
| RolePermissions | Optionally server-specific role permissions can be provided. |
| UserRolePermissions | Optionally the role permissions of the current Session can be provided. The value is server-specific and depends on the RolePermissions Attribute (if provided) and the current Session. |
| AccessRestrictions | Optionally server-specific access restrictions can be provided. |

#### Objects

For all Objects specified in this document, the Attributes named in Table 8 shall be set as specified in the Table 8. The definitions for the Attributes can be found in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model.

Table 8 – Common Object Attributes

| Attribute | Value |
| --- | --- |
| EventNotifier | Whether the Node can be used to subscribe to Events or not is server-specific. |

#### Variables

For all Variables specified in this document, the Attributes named in Table 9 shall be set as specified in the table. The definitions for the Attributes can be found in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model.

Table 9 – Common Variable Attributes

| Attribute | Value |
| --- | --- |
| MinimumSamplingInterval | Optionally, a server-specific minimum sampling interval is provided. |
| AccessLevel | The access level for Variables used for type definitions is server-specific, for all other Variables defined in this document, the access level shall allow reading; other settings are server-specific. |
| UserAccessLevel | The value for the UserAccessLevel Attribute is server-specific. It is assumed that all Variables can be accessed by at least one user. |
| Value | For Variables used as InstanceDeclarations, the value is server-specific; otherwise, it shall represent the value described in the text. |
| ArrayDimensions | If the ValueRank does not identify an array of a specific dimension (i.e., ValueRank <= 0) the ArrayDimensions can either be set to null or the Attribute is missing. This behaviour is server-specific. If the ValueRank specifies an array of a specific dimension (i.e., ValueRank > 0) then the ArrayDimensions Attribute shall be specified in the table defining the Variable. |
| Historizing | The value for the Historizing Attribute is server-specific. |
| AccessLevelEx | If the AccessLevelEx Attribute is provided, it shall have the bits 8, 9, and 10 set to 0, meaning that read and write operations on an individual Variable are atomic, and arrays can be partly written. |

#### VariableTypes

For all VariableTypes specified in this document, the Attributes named in Table 10 shall be set as specified in the table. The definitions for the Attributes can be found in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model.

Table 10 – Common VariableType Attributes

| Attributes | Value |
| --- | --- |
| Value | Optionally a server-specific default value can be provided. |
| ArrayDimensions | If the ValueRank does not identify an array of a specific dimension (i.e., ValueRank <= 0) the ArrayDimensions can either be set to null or the Attribute is missing. This behaviour is server-specific. If the ValueRank specifies an array of a specific dimension (i.e., ValueRank > 0) then the ArrayDimensions Attribute shall be specified in the table defining the VariableType. |

#### Methods

For all Methods specified in this document, the Attributes named in Table 11 shall be set as specified in the table. The definitions for the Attributes can be found in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model.

Table 11 – Common Method Attributes

| Attributes | Value |
| --- | --- |
| Executable | All Methods defined in this document shall be executable (Executable Attribute set to “True”), unless it is defined differently in the Method definition. |
| UserExecutable | The value of the UserExecutable Attribute is server-specific. It is assumed that all Methods can be executed by at least one user. |

### Structures

OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model differentiates between different kinds of Structures. The following conventions explain, how these Structures shall be defined.

The first kind are Structures without optional fields where none of the fields allows subtype (except fields with abstract DataTypes). Its definition is in Table 12.

Table 12 – Structures without optional fields where none of the fields allow subtypes

| Name | Type | Description |
| --- | --- | --- |
| <someStructure> | structure | Subtype of <someParentStructure> defined in … |
| SP1 | 0:Byte[] | Setpoint 1 |
| SP2 | 0:Byte[] | Setpoint 2 |

The second kind are Structures with optional fields where none of the fields allows subtypes (except fields with abstract DataTypes). Its definition is in Table 13.

Structures with fields that are optional have an “Optional” column. Fields that are optional have True set, otherwise False.

Table 13 – Structures with optional fields

| Name | Type | Description | Optional |
| --- | --- | --- | --- |
| <someStructure> | structure | Subtype of <someParentStructure> defined in … |  |
| SP1 | 0:Byte[] | Setpoint 1 | False |
| Optional Field_1 | 0:String | Some Text | True |

The third kind are Structures without optional fields where one or more of the fields allow subtypes. Its definition is in Table 14.

Structures with fields that allow subtypes have an “Allow Subtypes” column. Fields that allow subtypes have True set, otherwise False. Fields with abstract DataTypes can always be subtyped.

Table 14 – Structures where one or more of the fields allow subtypes

| Name | Type | Description | Allow Subtypes |
| --- | --- | --- | --- |
| <someStructure> | structure | Subtype of <someParentStructure> defined in … |  |
| SP1 | 0:Byte[] | Setpoint 1 | False |
| Allow Subtypes | 0:ByteString | Some Bytestring | True |

Fields with abstract DataTypes shall have True in the “Allow Subtypes” column.

It is not allowed to add both columns to combine optional fields and fields that allow subtypes in one structure.

# General information to Generators and OPC UA

## Introduction to Generators

A generator set converts fuel into electrical power on site: an engine drives an alternator, a controller starts, loads and protects the pair, and the support subsystems — fuel, cooling, lubrication, starting and exhaust aftertreatment — keep the engine able to run. Several sets may be paralleled onto one bus, and a transfer switch decides whether a load is fed from the utility or from the set.

Every one of those parts already reports data. The engine speaks SAE J1939 over a CAN bus, the controller exposes its own protocol, the transfer switch another. What is missing is a common description: an integrator wanting engine load, alternator power and the operating state of a set has to learn one vendor's map, then the next vendor's, and again for every fleet.

This document defines that common description as an OPC UA information model. It gives a generator set, its components, its ratings, its operating state machine and its protections a standard type, so that a Client reads the same BrowseNames, DataTypes and engineering units whatever equipment is behind them.

## Introduction to OPC Unified Architecture

This is an OPC UA introduction that can be used as is, shortened or enhanced as appropriate.

### What is OPC UA?

OPC UA is an open and royalty free set of standards designed as a universal communication protocol. While there are numerous communication solutions available, OPC UA has key advantages:

- A state of art security model (see OPC 10000-2, OPC Unified Architecture - Part 2: Security Model).

- A fault tolerant communication protocol.

- An information modelling framework that allows application developers to represent their data in a way that makes sense to them.

OPC UA has a broad scope which delivers for economies of scale for application developers. This means that a larger number of high-quality applications at a reasonable cost are available. When combined with semantic models such as Generators, OPC UA makes it easier for end users to access data via generic commercial applications.

The OPC UA model is scalable from small devices to ERP systems. OPC UA Servers process information locally and then provide that data in a consistent format to any application requesting data - ERP, MES, PMS, Maintenance Systems, HMI, Smartphone, or a standard Browser, for examples. For a more complete overview see OPC 10000-1, OPC Unified Architecture - Part 1: Overview and Concepts.

### Basics of OPC UA

As an open standard, OPC UA is based on standard internet technologies, like TCP/IP, HTTP, Web Sockets.

As an extensible standard, OPC UA provides a set of Services (see OPC 10000-4, OPC Unified Architecture - Part 4: Services) and a basic information model framework. This framework provides an easy manner for creating and exposing vendor defined information in a standard way. More importantly all OPC UA Clients are expected to be able to discover and use vendor-defined information. This means OPC UA users can benefit from the economies of scale that come with generic visualisation and historian applications. This specification is an example of an OPC UA Information Model designed to meet the needs of developers and users.

OPC UA Clients can be any consumer of data from another device on the network to browser based thin clients and ERP systems. The full scope of OPC UA applications is shown in Figure 1.

Figure 1 – The scope of OPC UA within an enterprise

OPC UA provides a robust and reliable communication infrastructure having mechanisms for handling lost messages, failover, heartbeat, etc. With its binary encoded data, it offers a high-performing data exchange solution. Security is built into OPC UA as security requirements become more and more important especially since environments are connected to the office network or the internet and attackers are starting to focus on automation systems.

### Information modelling in OPC UA

#### Concepts

OPC UA provides a framework that can be used to represent complex information as Objects in an AddressSpace which can be accessed with standard services. These Objects consist of Nodes connected by References. Different classes of Nodes convey different semantics. For example, a Variable Node represents a value that can be read or written. The Variable Node has an associated DataType that can define the actual value, such as a string, float, structure etc. It can also describe the Variable value as a variant. A Method Node represents a function that can be called. Every Node has a number of Attributes including a unique identifier called a NodeId and non-localized name called as BrowseName. An Object representing a ‘Reservation’ is shown in Figure 2.

Figure 2 – A basic Object in an OPC UA Address Space

Object and Variable Nodes represent instances and they always reference a TypeDefinition (ObjectType or VariableType) Node which describes their semantics and structure. Figure 3 illustrates the relationship between an instance and its TypeDefinition.

The type Nodes are templates that define all of the children that can be present in an instance of the type. In the example in Figure 3 the PersonType ObjectType defines two children: First Name and Last Name. All instances of PersonType are expected to have the same children with the same BrowseNames. Within a type the BrowseNames uniquely identify the children. This means Client applications can be designed to search for children based on the BrowseNames from the type instead of NodeIds. This eliminates the need for manual reconfiguration of systems if a Client uses types that multiple Servers implement.

OPC UA also supports the concept of sub-typing. This allows a modeller to take an existing type and extend it. There are rules regarding sub-typing defined in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model, but in general they allow the extension of a given type or the restriction of a DataType. For example, the modeller can decide that the existing ObjectType in some cases needs an additional Variable. The modeller can create a subtype of the ObjectType and add the Variable. A Client that is expecting the parent type can treat the new type as if it was of the parent type. Regarding DataTypes, subtypes can only restrict. If a Variable is defined to have a numeric value, a subtype could restrict it to a float.

Figure 3 – The relationship between Type Definitions and Instances

References allow Nodes to be connected in ways that describe their relationships. All References have a ReferenceType that specifies the semantics of the relationship. References can be hierarchical or non-hierarchical. Hierarchical references are used to create the structure of Objects and Variables. Non-hierarchical are used to create arbitrary associations. Applications can define their own ReferenceType by creating subtypes of an existing ReferenceType. Subtypes inherit the semantics of the parent but can add additional restrictions. Figure 4 depicts several References, connecting different Objects.

Figure 4 – Examples of References between Objects

The figures above use a notation that was developed for the OPC UA specification. The notation is summarized in Figure 5. UML representations can also be used; however, the OPC UA notation is less ambiguous because there is a direct mapping from the elements in the figures to Nodes in the AddressSpace of an OPC UA Server.

Figure 5 – The OPC UA Information Model notation

A complete description of the different types of Nodes and References can be found in OPC 10000-3, OPC Unified Architecture - Part 3: Address Space Model and the base structure is described in OPC 10000-5, OPC Unified Architecture - Part 5: Information Model.

The OPC UA specification defines a very wide range of functionality in its basic information model. It is not required that all Clients or Servers support all functionality in the OPC UA specifications. OPC UA includes the concept of Profiles, which segment the functionality into testable certifiable units. This allows the definition of functional subsets (that are expected to be implemented) within a companion specification. The Profiles do not restrict functionality, but generate requirements for a minimum set of functionalities (see OPC 10000-7, OPC Unified Architecture - Part 7: Profiles).

#### Namespaces

OPC UA allows information from many different sources to be combined into a single coherent AddressSpace. Namespaces are used to make this possible by eliminating naming and id conflicts between information from different sources. Each namespace in OPC UA has a globally unique string called a NamespaceUri which identifies a naming authority and a locally unique integer called a NamespaceIndex, which is an index into the Server's table of NamespaceUris. The NamespaceIndex is unique only within the context of a Session between an OPC UA Client and an OPC UA Server- the NamespaceIndex can change between Sessions and still identify the same item even though the NamespaceUri's location in the table has changed. The Services defined for OPC UA use the NamespaceIndex to specify the Namespace for qualified values.

There are two types of structured values in OPC UA that are qualified with NamespaceIndexes: NodeIds and QualifiedNames. NodeIds are locally unique (and sometimes globally unique) identifiers for Nodes. The same globally unique NodeId can be used as the identifier in a node in many Servers – the node's instance data can vary but its semantic meaning is the same regardless of the Server it appears in. This means Clients can have built-in knowledge of of what the data means in these Nodes. OPC UA Information Models generally define globally unique NodeIds for the TypeDefinitions defined by the Information Model.

QualifiedNames are non-localized names qualified with a Namespace. They are used for the BrowseNames of Nodes and allow the same names to be used by different information models without conflict. TypeDefinitions are not allowed to have children with duplicate BrowseNames; however, instances do not have that restriction.

#### Companion Specifications

An OPC UA companion specification for an industry specific vertical market describes an Information Model by defining ObjectTypes, VariableTypes, DataTypes and ReferenceTypes that represent the concepts used in the vertical market, and potentially also well-defined Objects as entry points into the AddressSpace.

# Use cases

The information model is transport‑neutral: it can be exposed over OPC UA client/server and, at scale, over OPC UA PubSub (OPC 10000‑14). This clause gives non‑normative recommendations for grouping the Variables of a generator set into PublishedDataSets (PDS) and WriterGroups so that a server can efficiently feed several classes of consumer. A server may publish any subset; the field paths below are BrowsePaths relative to a GeneratorSetType (or GeneratorSystemType) instance.

## General binding guidance

- A PublishedDataSet is a named list of published fields, each field bound to a Variable of the model (for example Alternator/TotalRealPower). Group fields by rate of change and consumer so that fast telemetry, slow nameplate/configuration, and event data travel in separate datasets and writer groups.

- Use one WriterGroup per publishing rate. Publish cyclic telemetry as delta frames with a periodic key frame; publish nameplate/configuration as low‑rate key frames or on change.

- Bind alarms and protection events to an event DataSet (the Part 14 event message mapping) rather than to a cyclic dataset.

- Expose DataSetMetaData including its ConfigurationVersion so subscribers can detect structural changes, and carry SourceTimestamp and StatusCode per field so analytics can reason about data quality and gaps.

- For multi‑set installations, a GeneratorSystemType writer publishes aggregated key indicators while each GeneratorSetType publishes its own detailed datasets.

## Operational observability

Real‑time monitoring, SCADA/HMI and remote operations. Low latency, small payloads, cyclic.

Table 15 – Operational observability

| PublishedDataSet | Suggested fields | Rate | Frame |
| --- | --- | --- | --- |
| GenSet.Live | OperatingState/CurrentState, OperatingMode, Engine/Speed, Engine/CoolantTemperature, Engine/OilPressure, Alternator/Frequency, Alternator/TotalRealPower, Alternator/AverageLineToLineVoltage, Alternator/AverageCurrent, FuelSystem/FuelLevel, StartingSystem/BatteryVoltage | 1 s | delta + 10 s key |
| GenSet.Status | GeneratorBreakerClosed, AvailableToLoad, RunRequest, LoadInhibit, Controller/InAutoMode, DeviceHealth | on change | key |

## Analytics for predictive maintenance

Trending of wear‑ and condition‑related signals together with diagnostic codes and usage counters; historized. Moderate rate.

Table 16 – Analytics for predictive maintenance

| PublishedDataSet | Suggested fields | Rate |
| --- | --- | --- |
| GenSet.Condition | Engine/OilPressure, Engine/OilTemperature, Engine/CoolantTemperature, Engine/ExhaustGasTemperature, Engine/IntakeManifoldPressure, LubricationSystem/OilFilterDifferentialPressure, Alternator/WindingTemperature1..3, Alternator/BearingTemperatureDriveEnd, Alternator/BearingTemperatureNonDriveEnd, FuelSystem/FuelPressure | 1–10 s |
| GenSet.Usage | Engine/EngineHours, Engine/NumberOfStarts, StartingSystem/StartAttempts, Alternator/TotalRealEnergy, FuelSystem/TotalFuelConsumed | 1 min / on change |
| GenSet.Diagnostics | Engine/CanInterface/ActiveDiagnosticTroubleCodes, Engine/CanInterface/PreviouslyActiveDiagnosticTroubleCodes, Engine/CanInterface/AmberWarningLamp, Engine/CanInterface/RedStopLamp | on change |

Predictive models correlate the condition signals with usage counters and DTC history to forecast wear (bearings, injectors, cooling and lubrication systems) and to schedule service before failure.

## Analytics for anomaly detection

High‑resolution, correlated electrical and mechanical signals for baseline modelling and deviation/outlier detection (phase imbalance, load‑vs‑fuel drift, incipient faults).

Table 17 – Analytics for anomaly detection

| PublishedDataSet | Suggested fields | Rate |
| --- | --- | --- |
| GenSet.HiRes | Engine/Speed, Engine/PercentLoad, Engine/FuelRate, Alternator/Frequency, Alternator/TotalRealPower, Alternator/TotalReactivePower, and per‑phase Alternator/L1..L3/Current, .../LineToNeutralVoltage, .../PowerFactor | 100 ms – 1 s |

## Energy and load management

Load sharing, peak shaving, demand response and grid‑services coordination across a bus or fleet.

Table 18 – Energy and load management

| PublishedDataSet | Suggested fields | Rate |
| --- | --- | --- |
| System.Load | ParallelingController/TotalBusRealPower, .../TotalBusReactivePower, .../BusFrequency, .../BusVoltage, .../LoadSharePercent, .../AvailableCapacity, .../SpinningReserve, .../UtilityImportPower, .../UtilityExportPower | 200 ms – 1 s |
| GenSet.Power | Alternator/TotalRealPower, Alternator/LoadPercent, Ratings/<Rating>/RatedRealPower | 1 s |

## Alarm and event distribution

Protection and condition events for operators, CMMS/EAM systems and safety functions.

Table 19 – Alarm and event distribution

| Event DataSet | Source | Delivery |
| --- | --- | --- |
| GenSet.Events | GeneratorProtectionAlarmType events (ProtectionFunction, ProtectionAction, IsShutdown, Spn, Fmi, SubsystemName) plus the standard AcknowledgeableConditionType fields, including the authoritative Part 9 Severity; GeneratorAlarmSeverity is a compatibility projection only | event‑driven, reliable, with keep‑alive |

## Fleet monitoring and compliance

Multi‑site supervision, contractual reporting and regulatory / emergency‑power compliance (for example NFPA 110 test records and emissions reporting).

Table 20 – Fleet monitoring and compliance

| PublishedDataSet | Suggested fields | Rate |
| --- | --- | --- |
| GenSet.Nameplate | Identification/Manufacturer, Identification/Model, Identification/SerialNumber, Identification/EngineModel, Identification/AlternatorModel, Identification/RatedRealPower, Identification/EmissionsStandard, Application, Controller/FirmwareVersion, Controller/ConfigurationVersion | on change / daily key |
| GenSet.Compliance | EmissionsStandard, Engine/Aftertreatment/AftertreatmentState, Engine/Aftertreatment/DefLevel, Engine/Aftertreatment/DpfSootLoad, Engine/EngineHours, FuelSystem/TotalFuelConsumed (test runs are recorded via the StartTest method and protection/condition events) | periodic / event |
| System.Fleet | per set OperatingState/CurrentState and Alternator/TotalRealPower; system TotalSystemLoad, TotalSystemCapacity, NumberOfGeneratorSets | 1–10 s |

# Generators information model overview

## What is a generator set

A generator set is simultaneously two things: an asset with a nameplate, health and a life‑cycle; and a machine whose core is an internal‑combustion engine coupled to an alternator. Sizes span four orders of magnitude of power. A small residential unit may produce ~13 kW on natural gas; a large industrial set built on a ~95 L V16 high‑speed diesel engine can deliver 3.0–3.75 MW, is the size of a small house, and consumes on the order of 130–210 US gal/h of diesel at full load. Between those extremes lie commercial standby, data‑center, healthcare, rental/mobile and marine products.

Whatever the size, every set exposes broadly the same information: identity, ratings, an operating state and mode, engine and alternator telemetry, fuel/cooling/lubrication/battery status, protections/alarms and start/stop control. This specification captures that common information once, so that a single client can monitor and (where permitted) control any conforming set.

## Relationship to other companion specifications

This model is layered on established OPC UA building blocks rather than reinventing them:

- DI (Devices). GeneratorSetType derives from the DI DeviceType, inheriting a complete nameplate (Manufacturer, Model, SerialNumber, HardwareRevision, SoftwareRevision, DeviceRevision, RevisionCounter, …) and DeviceHealth (NORMAL/FAILURE/CHECK_FUNCTION/OFF_SPEC/MAINTENANCE_REQUIRED). Each subsystem (engine, alternator, fuel system, …) derives from the DI ComponentType, the standard base for an identifiable component of a device.

- Machinery. Every set carries the Machinery building blocks so that it is discoverable and interoperable alongside other machines: an Identification add‑in (a GeneratorIdentificationType, which specialises the Machinery MachineIdentificationType) and a MachineryBuildingBlocks folder holding the generic MachineryItemState and MachineryOperationMode state machines.

- Part 9 (Alarms & Conditions). Protection events are modelled by GeneratorProtectionAlarmType, a subtype of OffNormalAlarmType.

- Part 5 / Part 16 (State machines). The detailed run states of a set are modelled by GeneratorStateMachineType, a FiniteStateMachineType.

## Namespaces used by the model

Table 21 – Namespaces used by the model

| Index | Namespace URI | Role |
| --- | --- | --- |
| 0 | http://opcfoundation.org/UA/ | OPC UA core |
| 1 | http://opcfoundation.org/UA/Generators/ | This specification |
| 2 | http://opcfoundation.org/UA/DI/ | Devices |
| 3 | http://opcfoundation.org/UA/Machinery/ | Machinery |

Numeric NodeIds in namespace 1 are allocated as follows: ObjectTypes 1001–1099, DataTypes 3001–3099 (enumerations) and 3050+ (structures), EnumStrings properties datatype‑id + 900, and all remaining instance declarations (members, method arguments, state‑machine states and transitions) sequentially from 6001.

## Information model architecture

The AddressSpace figures in this document use the OPC UA graphical notation of OPC 10000-3. A Node of an instance NodeClass — Object, Variable or View — is a plain rectangle, a Method is a rounded rectangle, and a type — ObjectType, VariableType, ReferenceType or DataType — is a rectangle standing on a shadow. An abstract type is set in italics, and a Node whose BrowseName is a placeholder is written in angle brackets. A HasTypeDefinition reference carries a solid arrowhead; a HasComponent reference is the plain unlabelled arrow; every other ReferenceType is drawn with its BrowseName on the arrow. A figure shows the part of the model its clause describes, never the whole of it.

Figure 6 – Graphical notation used by the AddressSpace figures

## Composition of a generator set

Figure 7 – Composition of a generator set

A multi‑set installation (data‑center, healthcare, campus) is represented by GeneratorSystemType, which aggregates one or more GeneratorSetType instances, an optional ParallelingControllerType and one or more AutomaticTransferSwitchType instances.

## Design rationale

- Asset + machine, not either/or. Deriving from DeviceType gives the set an asset identity and health; adding the Machinery building blocks makes it discoverable as a machine. The Identification add‑in intentionally mirrors a few nameplate fields already present on DeviceType; the add‑in is the cross‑vendor, Machinery‑standard location, whereas the inherited DeviceType fields are the DI‑native location. Servers may populate either or both, but where both are present the equivalent fields (Manufacturer, Model, SerialNumber, ProductInstanceUri) shall carry the same value.

- Composition over deep inheritance (OPC 11030 §7.2.4). Subsystems are separate ComponentType subtypes referenced by HasComponent, so a set can be assembled from exactly the components it has (a home‑standby air‑cooled unit omits the paralleling controller; a Tier 4 diesel adds ExhaustAftertreatment).

- Physical quantities use AnalogUnitType with machine‑readable units. Every measured value is typed AnalogUnitType and carries an EngineeringUnits property whose value is a standard UNECE/CEFACT unit (e.g. r/min, kPa, °C, kW, Hz), so a client can discover the unit from the type model alone. A server may override this default at instance level to reflect the unit it actually reports (e.g. psi, gal/h, °F); the value range (EURange) is left to the instance.

- The engine's CAN/J1939 interface is explicit. Because a generator is "part engine with a CAN bus interface", the engine exposes a dedicated J1939DiagnosticInterfaceType add‑in carrying the network parameters, the J1939 lamp status and the active/previously‑active DTC arrays.

## Organisation of the ObjectTypes

The full member tables for every type are in Annex A. This clause summarises the intent of each type.

## The generator set

The central type. Mandatory content: OperatingState (a GeneratorStateMachineType), OperatingMode, the Engine, Alternator and Controller components, the Identification add‑in and a Ratings folder. Optional content: fuel/cooling/lubrication/starting subsystems, EmissionsStandard, Application, breaker and readiness signals (GeneratorBreakerClosed, GeneratorBreakerAvailable, RemoteStartInput, RunRequest, LoadInhibit, AvailableToLoad), and the Machinery building blocks. Methods: Start (no argument — starts in the current mode), Stop, EmergencyStop, ResetFaults, SetOperatingMode, StartTest. The type GeneratesEvent GeneratorProtectionAlarmType.

The figure shows the Mandatory content — what a conforming generator set always has. The optional subsystems, signals and Methods listed above are omitted; Annex A carries the full member list.

<!-- model-figure: root=ns=1;i=1001 require=mandatory external=DeviceType -->

Figure 8 – The Mandatory content of a generator set

## The engine and the CAN bus interface

EngineType exposes the classic engine telemetry — Speed (SPN 190), OilPressure (SPN 100), CoolantTemperature (SPN 110), FuelRate (SPN 183), EngineHours (SPN 247), boost, exhaust and intake temperatures, percent load/torque, etc. The referenced SPN for each variable is recorded in the variable description so that a gateway can map J1939 signals directly onto the model.

The engine's CanInterface (a J1939DiagnosticInterfaceType) models the network itself: ProtocolName ("SAE J1939"), NetworkName, SourceAddress, Baudrate (250 000 or 500 000 bit/s), BusState, the four J1939 DM1 lamp statuses (AmberWarningLamp, RedStopLamp, MalfunctionIndicatorLamp, ProtectLamp, each a J1939LampStatusEnum conveying Off / On / SlowFlash / FastFlash), and the ActiveDiagnosticTroubleCodeDetails (DM1) and PreviouslyActiveDiagnosticTroubleCodeDetails (DM2) arrays of DiagnosticTroubleCodeDataType. Each DTC carries Spn, Fmi, OccurrenceCount, SourceAddress/SourceName (so faults from multiple ECUs on the bus remain distinguishable) and an optional ProtectionAction. The method ClearPreviouslyActiveDtcs corresponds to J1939 DM3/DM11.

The legacy ActiveDiagnosticTroubleCodes and PreviouslyActiveDiagnosticTroubleCodes arrays of DiagnosticTroubleCodeType remain for compatibility. A new Server should expose the *Details members. Where both forms are present, they shall describe the same DTCs in the same order. The legacy Severity field keeps its published semantics and shall not be derived mechanically from ProtectionAction; a Server populates it only when its legacy classification is true for the reported DTC.

## The alternator and its phases

AlternatorType provides aggregate values — Frequency, TotalRealPower/TotalReactivePower/TotalApparentPower, average voltages and current, AveragePowerFactor, TotalRealEnergy, LoadPercent, winding and bearing temperatures, Connection, ExcitationType, NumberOfPoles — and three phase objects (L1, L2, L3, each an AlternatorPhaseType) carrying per‑phase voltage, current, power and power factor. Single‑phase sets populate only L1 (mandatory); three‑phase sets populate all three.

## Support subsystems

FuelSystemType (fuel type/level/rate/pressure, gas supply pressure, runtime remaining, DEF for aftertreatment, water‑in‑fuel), CoolingSystemType (coolant temperature/level/pressure, cooling method, radiator fan and jacket‑water heater), LubricationSystemType (oil pressure/temperature/level, filter Δp) and StartingSystemType (battery voltage/charging current, charger status, start attempts) model the balance‑of‑plant. All are optional so the type fits both a bare air‑cooled residential set and a fully instrumented industrial set.

## The controller

Represents the control panel. Carries controller identity (ControllerFamily, FirmwareVersion, ApplicationSoftwareVersion, ConfigurationVersion), operating annunciation (InAutoMode, NotInAuto), remote enablement (RemoteStartEnabled, RemoteControlEnabled) and remote‑monitoring status (CloudConnected, ModbusEnabled, SignalStrength).

## Ratings

Because a set is usually certified for several ISO 8528 duties, ratings are modelled as a placeholder list. The Ratings folder on GeneratorSetType contains zero or more GeneratorRatingType objects, each with an ApplicationRating (ESP/PRP/COP/LTP/DCC) and the rated power, voltage, current, frequency, speed, power factor, phase count and reference ambient/altitude.

## The operating state machine

OperatingState is a finite state machine with twelve states and the transitions shown below. It is the detailed, generator‑specific complement to the generic Machinery MachineryItemState.

Figure 9 – The generator operating state machine

## Operating modes

OperatingMode (a GeneratorOperatingModeEnum value) is the authoritative control-panel selector: Off, Manual, Auto, Test, Exercise, RemoteStart, Maintenance, Lockout. SetOperatingMode changes this value; a Server shall not accept an independent command that changes the optional Machinery MachineryOperationMode state machine.

Where MachineryOperationMode is present under MachineryBuildingBlocks, it is a derived interoperability projection. Its CurrentState shall equal the row below for the authoritative OperatingMode value:

Table 22 – Operating modes

| OperatingMode | MachineryOperationMode.CurrentState |
| --- | --- |
| Maintenance | Maintenance |
| Test or Exercise | Setup |
| Manual, Auto or RemoteStart | Processing |
| Off or Lockout | None |

The projection does not create a second source of truth. OperatingState and MachineryItemState separately report whether the selected mode is executing, idle, unavailable or faulted. If the two operation-mode representations disagree, OperatingMode decides and the MachineryOperationMode state is incorrect.

## Protections and alarms

GeneratorProtectionAlarmType (subtype of OffNormalAlarmType) reports any protection or shutdown condition. Its ProtectionFunction property (a GeneratorProtectionFunctionEnum with 64 values — low oil pressure, high coolant temperature, overspeed, overcrank, over/under voltage and frequency, overload, reverse power, ground fault, emergency stop, aftertreatment faults, ATS/breaker failures, …) identifies the condition. ProtectionAction classifies the automatic response requested by that function: no automatic action, warning, derate, shutdown, electrical trip, lockout or emergency stop.

The inherited Part 9 Severity field is the sole authority for event urgency and shall be populated independently of ProtectionAction. IsShutdown reports the actual engine outcome and shall not be inferred from ProtectionAction: for example, an alarm may request Shutdown while IsShutdown remains false until shutdown completes or if the action fails. Spn, Fmi and SubsystemName add origin context.

The legacy GeneratorAlarmSeverity property remains for compatibility. A new Server should expose ProtectionAction instead. GeneratorAlarmSeverity keeps its published semantics and shall not be derived mechanically from ProtectionAction; for example, legacy Shutdown is valid only when the engine is shut down, not merely when shutdown was requested. Neither property changes the meaning or authority of inherited Severity.

Because the type is an OffNormalAlarmType, the normal state is "healthy / not tripped": on an instance, the inherited NormalState references the node representing the healthy value, InputNode references the supervised input (e.g. the shutdown latch or the measured variable), and SourceNode references the owning GeneratorSetType or subsystem so that clients can locate the origin. Analog limit conditions (e.g. over/under voltage) may additionally be surfaced with standard ExclusiveLevelAlarmType instances on the corresponding measured variables.

## Transfer switches and paralleling

AutomaticTransferSwitchType (a DeviceType) models an ATS: Position, OperatingState, TransitionType, two structured sources (Source1, Source2, each a TransferSwitchSourceType carrying Available, Acceptable, Voltage, Frequency and PhaseRotation), PreferredSource, source connection flags, TransferInhibited/TransferInhibitReason, ratings, load metering, transfer timers and counters, and the Transfer/Retransfer/InhibitTransfer methods. ParallelingControllerType models synchronising and load sharing across a common bus: SystemState, bus voltage/frequency/power, synchronising deltas (SynchronizationAngle, SlipFrequency, voltage/frequency difference, SyncCheckPermissive, DeadBus), load‑share and capacity values, breaker states, utility import/export, and the ConnectToBus/DisconnectFromBus methods.

## The generator system

Aggregates a paralleled plant: a mandatory GeneratorSets folder of GeneratorSetType instances, an optional ParallelingController, an optional TransferSwitches folder, and system totals (NumberOfGeneratorSets, TotalSystemCapacity, TotalSystemLoad, RedundancyScheme).

## Organisation of the DataTypes

Eighteen enumerations and two structures are defined; see Annex A for the full value lists. The enumerations are extensible (each provides an Other/Unknown member where appropriate) and cover fuel types, application/duty ratings, electrical connection, excitation, cooling method, aspiration, emissions standard, CAN bus state, J1939 lamp status, transfer-switch position/transition/state, generator protection action, the 64-value protection-function list, paralleling-system state and aftertreatment state. The DiagnosticTroubleCodeDataType structure carries a single SAE J1939 DTC (Spn, Fmi, OccurrenceCount, ConversionMethod, Active, SourceAddress, SourceName, optional ProtectionAction, Description). DiagnosticTroubleCodeType and AlarmSeverityEnum are retained only as compatibility types.

## Coverage of the industry

The model is vendor‑neutral. The following mapping shows how representative product tiers across the generator industry are expressed with the types defined here; products from any manufacturer map the same way.

Table 23 – Coverage of the industry

| Product tier | Represented by |
| --- | --- |
| Residential / home standby (~10–60 kW, air‑ or liquid‑cooled, natural gas / LPG) | GeneratorSetType with an air‑ or liquid‑cooled CoolingSystem, FuelType = NaturalGas/Propane, and a single‑phase alternator (L1 only) |
| Commercial & industrial diesel (up to ~3.75 MW) | GeneratorSetType with a high‑power EngineType, three‑phase AlternatorType, ExhaustAftertreatment (Tier 4 / Stage V), and multiple GeneratorRatingType (Standby / Prime) |
| Natural‑gas / lean‑burn (~55 kW–2 MW, CHP / continuous) | GeneratorSetType with FuelType = NaturalGas/Biogas/LandfillGas, FuelSystem.GasSupplyPressure, and ApplicationRating = Continuous |
| Data‑center (multi‑MW, N+1 / 2N, medium‑voltage bus) | GeneratorSystemType aggregating sets with ApplicationRating = DataCenterContinuous, a ParallelingControllerType, and a RedundancyScheme |
| Healthcare / life‑safety (NFPA 110 Level 1) | GeneratorSetType + AutomaticTransferSwitchType; readiness via StartingSystem, FuelSystem.RuntimeRemaining and Controller.InAutoMode |
| Rental / mobile / towable (Tier 4 Final) | GeneratorSetType with ExhaustAftertreatment (DEF / DPF / SCR) and Application = Rental |
| Control panels & cloud monitoring | GeneratorControllerType (ControllerFamily, firmware/config versions, CloudConnected, ModbusEnabled) |
| Transfer switches (open / closed / soft‑load, bypass‑isolation) | AutomaticTransferSwitchType (TransitionType, structured Source1/Source2) |
| Paralleling switchgear / master control | ParallelingControllerType + GeneratorSystemType |

# OPC UA ObjectTypes

## GeneratorIdentificationType

Identification and nameplate of a generator set. Extends the Machinery MachineIdentificationType with generator-specific nameplate data.

Table 24 – GeneratorIdentificationType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorIdentificationType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 3:MachineIdentificationType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | SpecificationNumber | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | ProductFamily | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | EngineModel | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | EngineSerialNumber | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | AlternatorModel | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | AlternatorSerialNumber | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | ControllerModel | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | FuelType | FuelTypeEnum | 0:PropertyType | O |
| 0:HasProperty | Variable | EmissionsStandard | EmissionsStandardEnum | 0:PropertyType | O |
| 0:HasComponent | Variable | RatedRealPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedApparentPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedFrequency | 0:Double | 0:AnalogUnitType | O |
| 0:HasProperty | Variable | SoundRatingAt7m | 0:Double | 0:PropertyType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Identification |  |  |  |  |  |

## GeneratorStateMachineType

Finite state machine describing the operating state of a generator set: Off, Ready, Starting, Warmup, Running, Loaded, Synchronizing, Paralleled, Cooldown, Stopping, Fault and EmergencyStopped.

Table 25 – GeneratorStateMachineType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorStateMachineType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:FiniteStateMachineType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Object | Off |  | 0:InitialStateType |  |
| 0:HasComponent | Object | Ready |  | 0:StateType |  |
| 0:HasComponent | Object | Starting |  | 0:StateType |  |
| 0:HasComponent | Object | Warmup |  | 0:StateType |  |
| 0:HasComponent | Object | Running |  | 0:StateType |  |
| 0:HasComponent | Object | Loaded |  | 0:StateType |  |
| 0:HasComponent | Object | Synchronizing |  | 0:StateType |  |
| 0:HasComponent | Object | Paralleled |  | 0:StateType |  |
| 0:HasComponent | Object | Cooldown |  | 0:StateType |  |
| 0:HasComponent | Object | Stopping |  | 0:StateType |  |
| 0:HasComponent | Object | Fault |  | 0:StateType |  |
| 0:HasComponent | Object | EmergencyStopped |  | 0:StateType |  |
| 0:HasComponent | Object | OffToReady |  | 0:TransitionType |  |
| 0:HasComponent | Object | ReadyToStarting |  | 0:TransitionType |  |
| 0:HasComponent | Object | ReadyToOff |  | 0:TransitionType |  |
| 0:HasComponent | Object | StartingToWarmup |  | 0:TransitionType |  |
| 0:HasComponent | Object | StartingToFault |  | 0:TransitionType |  |
| 0:HasComponent | Object | WarmupToRunning |  | 0:TransitionType |  |
| 0:HasComponent | Object | RunningToLoaded |  | 0:TransitionType |  |
| 0:HasComponent | Object | RunningToSynchronizing |  | 0:TransitionType |  |
| 0:HasComponent | Object | SynchronizingToParalleled |  | 0:TransitionType |  |
| 0:HasComponent | Object | SynchronizingToRunning |  | 0:TransitionType |  |
| 0:HasComponent | Object | ParalleledToLoaded |  | 0:TransitionType |  |
| 0:HasComponent | Object | LoadedToCooldown |  | 0:TransitionType |  |
| 0:HasComponent | Object | RunningToCooldown |  | 0:TransitionType |  |
| 0:HasComponent | Object | CooldownToStopping |  | 0:TransitionType |  |
| 0:HasComponent | Object | StoppingToOff |  | 0:TransitionType |  |
| 0:HasComponent | Object | RunningToFault |  | 0:TransitionType |  |
| 0:HasComponent | Object | LoadedToFault |  | 0:TransitionType |  |
| 0:HasComponent | Object | ParalleledToFault |  | 0:TransitionType |  |
| 0:HasComponent | Object | FaultToOff |  | 0:TransitionType |  |
| 0:HasComponent | Object | RunningToEmergencyStopped |  | 0:TransitionType |  |
| 0:HasComponent | Object | LoadedToEmergencyStopped |  | 0:TransitionType |  |
| 0:HasComponent | Object | ParalleledToEmergencyStopped |  | 0:TransitionType |  |
| 0:HasComponent | Object | EmergencyStoppedToOff |  | 0:TransitionType |  |
| Conformance Units |  |  |  |  |  |
| GEN-StateMachine |  |  |  |  |  |

## J1939DiagnosticInterfaceType

The engine CAN bus / SAE J1939 diagnostic interface. Surfaces the network connection parameters, J1939 lamp status and active/previously-active diagnostic trouble codes reported by the engine ECU.

Table 26 – J1939DiagnosticInterfaceType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:J1939DiagnosticInterfaceType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:BaseObjectType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | ProtocolName | 0:String | 0:PropertyType | M |
| 0:HasProperty | Variable | NetworkName | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | SourceAddress | 0:Byte | 0:PropertyType | O |
| 0:HasProperty | Variable | Baudrate | 0:UInt32 | 0:PropertyType | O |
| 0:HasComponent | Variable | BusState | CanBusStateEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | AmberWarningLamp | J1939LampStatusEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RedStopLamp | J1939LampStatusEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | MalfunctionIndicatorLamp | J1939LampStatusEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | ProtectLamp | J1939LampStatusEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | ActiveDiagnosticTroubleCodes | DiagnosticTroubleCodeType[] | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | PreviouslyActiveDiagnosticTroubleCodes | DiagnosticTroubleCodeType[] | 0:BaseDataVariableType | O |
| 0:HasComponent | Method | ClearPreviouslyActiveDtcs |  |  | O |
| 0:HasComponent | Variable | ActiveDiagnosticTroubleCodeDetails | DiagnosticTroubleCodeDataType[] | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | PreviouslyActiveDiagnosticTroubleCodeDetails | DiagnosticTroubleCodeDataType[] | 0:BaseDataVariableType | O |
| Conformance Units |  |  |  |  |  |
| GEN-CANbus |  |  |  |  |  |

### ClearPreviouslyActiveDtcs

Clear previously active diagnostic trouble codes (J1939 DM3/DM11).

Signature

ClearPreviouslyActiveDtcs ();

## ExhaustAftertreatmentType

Exhaust aftertreatment subsystem (DPF/SCR/DEF) for Tier 4 / Stage V engines.

Table 27 – ExhaustAftertreatmentType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:ExhaustAftertreatmentType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | AftertreatmentState | AftertreatmentStateEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | DefLevel | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | DefTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | DefQuality | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | DpfSootLoad | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | DpfAshLoad | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | ExhaustGasTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RegenerationRequired | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RegenerationInhibited | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Method | InitiateRegeneration |  |  | O |
| 0:HasComponent | Method | InhibitRegeneration |  |  | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

### InitiateRegeneration

Request a manual DPF regeneration.

Signature

InitiateRegeneration ();

### InhibitRegeneration

Enable or disable the inhibit of automatic regeneration.

Signature

InhibitRegeneration (

[in]  0:Boolean      Inhibit);

Table 28 – InhibitRegeneration Method Arguments

| Argument | Description |
| --- | --- |
| Inhibit | TRUE to inhibit regeneration. |

Table 29 – InhibitRegeneration Method AddressSpace definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | InhibitRegeneration |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | ModellingRule |
| 0:HasProperty | Variable | 0:InputArguments | 0:Argument[] | 0:PropertyType | 0:Mandatory |

## EngineType

The prime-mover engine of a generator set. Exposes engine telemetry, typically obtained over the CAN bus / SAE J1939 interface, and identification.

Table 30 – EngineType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:EngineType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | Speed | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | PercentLoad | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | PercentTorque | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | OilPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | OilTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | CoolantTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | CoolantPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FuelRate | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FuelTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | IntakeManifoldPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | IntakeManifoldTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | ExhaustGasTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | BarometricPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | EngineHours | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | NumberOfStarts | 0:UInt32 | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | Aspiration | AspirationEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | Displacement | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | CylinderCount | 0:UInt16 | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RatedSpeed | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Object | CanInterface |  | J1939DiagnosticInterfaceType | O |
| 0:HasComponent | Object | Aftertreatment |  | ExhaustAftertreatmentType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## AlternatorPhaseType

Per-phase electrical measurements of the alternator output.

Table 31 – AlternatorPhaseType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AlternatorPhaseType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:BaseObjectType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | LineToNeutralVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | LineToLineVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | Current | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | RealPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | ReactivePower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | ApparentPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | PowerFactor | 0:Double | 0:BaseDataVariableType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## AlternatorType

The alternator (generator end) that converts mechanical power into AC electrical power. Exposes aggregate and per-phase electrical measurements.

Table 32 – AlternatorType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AlternatorType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | Frequency | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | AverageLineToLineVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | AverageLineToNeutralVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | AverageCurrent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TotalRealPower | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | TotalReactivePower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TotalApparentPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | AveragePowerFactor | 0:Double | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | TotalRealEnergy | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | LoadPercent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | WindingTemperature1 | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | WindingTemperature2 | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | WindingTemperature3 | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | BearingTemperatureDriveEnd | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | BearingTemperatureNonDriveEnd | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | Connection | ElectricalConnectionEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | ExcitationType | ExcitationTypeEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | NumberOfPoles | 0:UInt16 | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | VoltageSetpoint | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FieldCurrent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Object | L1 |  | AlternatorPhaseType | M |
| 0:HasComponent | Object | L2 |  | AlternatorPhaseType | O |
| 0:HasComponent | Object | L3 |  | AlternatorPhaseType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## FuelSystemType

The fuel storage and delivery subsystem of a generator set.

Table 33 – FuelSystemType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:FuelSystemType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | FuelType | FuelTypeEnum | 0:BaseDataVariableType | M |
| 0:HasComponent | Variable | FuelLevel | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FuelVolume | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FuelConsumptionRate | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FuelPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FuelTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | GasSupplyPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RuntimeRemaining | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TotalFuelConsumed | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | WaterInFuel | 0:Boolean | 0:BaseDataVariableType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## CoolingSystemType

The engine cooling subsystem of a generator set.

Table 34 – CoolingSystemType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:CoolingSystemType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | CoolantTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | CoolantLevel | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | CoolantPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | CoolingMethod | CoolingMethodEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | AmbientTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RadiatorFanRunning | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | JacketWaterHeaterActive | 0:Boolean | 0:BaseDataVariableType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## LubricationSystemType

The engine lubrication subsystem of a generator set.

Table 35 – LubricationSystemType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:LubricationSystemType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | OilPressure | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | OilTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | OilLevel | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | OilFilterDifferentialPressure | 0:Double | 0:AnalogUnitType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## StartingSystemType

The starting/battery subsystem of a generator set.

Table 36 – StartingSystemType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:StartingSystemType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | BatteryVoltage | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | BatteryChargingCurrent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | BatteryChargerActive | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | StartAttempts | 0:UInt32 | 0:BaseDataVariableType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## GeneratorControllerType

The generator set control panel. Provides controller identity, mode/state visibility and remote-monitoring status.

Table 37 – GeneratorControllerType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorControllerType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | ControllerFamily | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | FirmwareVersion | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | ApplicationSoftwareVersion | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | ConfigurationVersion | 0:String | 0:PropertyType | O |
| 0:HasComponent | Variable | InAutoMode | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | NotInAuto | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RemoteStartEnabled | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RemoteControlEnabled | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | CloudConnected | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | ModbusEnabled | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | SignalStrength | 0:Double | 0:AnalogUnitType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Components |  |  |  |  |  |

## GeneratorRatingType

A single nameplate power rating point of a generator set for a given application/duty (ISO 8528).

Table 38 – GeneratorRatingType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorRatingType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:BaseObjectType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | ApplicationRating | GeneratorApplicationRatingEnum | 0:BaseDataVariableType | M |
| 0:HasComponent | Variable | RatedRealPower | 0:Double | 0:AnalogUnitType | M |
| 0:HasComponent | Variable | RatedApparentPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedPowerFactor | 0:Double | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RatedVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedCurrent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedFrequency | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | RatedSpeed | 0:Double | 0:AnalogUnitType | O |
| 0:HasProperty | Variable | PhaseCount | 0:Byte | 0:PropertyType | O |
| 0:HasComponent | Variable | Connection | ElectricalConnectionEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | AmbientTemperature | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | Altitude | 0:Double | 0:AnalogUnitType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Rating |  |  |  |  |  |

## GeneratorSetType

A generator set (GenSet): a complete electrical power generation asset composed of a prime-mover engine, an alternator, a fuel system, cooling, lubrication, starting and control subsystems. Applicable to the whole industry, from small home-standby units to house-sized multi-megawatt industrial sets.

Table 39 – GeneratorSetType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorSetType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:DeviceType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasAddIn | Object | Identification |  | GeneratorIdentificationType | M |
| 0:HasAddIn | Object | MachineryBuildingBlocks |  | 0:FolderType | O |
| 0:HasComponent | Object | OperatingState |  | GeneratorStateMachineType | M |
| 0:HasComponent | Variable | OperatingMode | GeneratorOperatingModeEnum | 0:BaseDataVariableType | M |
| 0:HasComponent | Variable | EmissionsStandard | EmissionsStandardEnum | 0:BaseDataVariableType | O |
| 0:HasProperty | Variable | Application | 0:String | 0:PropertyType | O |
| 0:HasComponent | Variable | GeneratorBreakerClosed | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | GeneratorBreakerAvailable | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RemoteStartInput | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RunRequest | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | LoadInhibit | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | AvailableToLoad | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Object | Engine |  | EngineType | M |
| 0:HasComponent | Object | Alternator |  | AlternatorType | M |
| 0:HasComponent | Object | Controller |  | GeneratorControllerType | M |
| 0:HasComponent | Object | FuelSystem |  | FuelSystemType | O |
| 0:HasComponent | Object | CoolingSystem |  | CoolingSystemType | O |
| 0:HasComponent | Object | LubricationSystem |  | LubricationSystemType | O |
| 0:HasComponent | Object | StartingSystem |  | StartingSystemType | O |
| 0:HasComponent | Object | Ratings |  | 0:FolderType | M |
| 0:HasComponent | Method | Start |  |  | O |
| 0:HasComponent | Method | Stop |  |  | O |
| 0:HasComponent | Method | EmergencyStop |  |  | O |
| 0:HasComponent | Method | ResetFaults |  |  | O |
| 0:HasComponent | Method | SetOperatingMode |  |  | O |
| 0:HasComponent | Method | StartTest |  |  | O |
| 0:GeneratesEvent | ObjectType | GeneratorProtectionAlarmType |  |  |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

### Start

Command the set to start in the current operating mode.

Signature

Start ();

### Stop

Command a normal stop (with cooldown).

Signature

Stop ();

### EmergencyStop

Command an immediate emergency stop.

Signature

EmergencyStop ();

### ResetFaults

Reset latched faults / lockout.

Signature

ResetFaults ();

### SetOperatingMode

Set the control-panel selector mode.

Signature

SetOperatingMode (

[in]  GeneratorOperatingModeEnum Mode);

Table 40 – SetOperatingMode Method Arguments

| Argument | Description |
| --- | --- |
| Mode | The requested operating mode. |

Table 41 – SetOperatingMode Method AddressSpace definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | SetOperatingMode |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | ModellingRule |
| 0:HasProperty | Variable | 0:InputArguments | 0:Argument[] | 0:PropertyType | 0:Mandatory |

### StartTest

Start a test run for a given duration.

Signature

StartTest (

[in]  0:UInt32       DurationMinutes,

[in]  0:Boolean      WithLoad);

Table 42 – StartTest Method Arguments

| Argument | Description |
| --- | --- |
| DurationMinutes | Test duration in minutes. |
| WithLoad | TRUE to run the test with load. |

Table 43 – StartTest Method AddressSpace definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | StartTest |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | ModellingRule |
| 0:HasProperty | Variable | 0:InputArguments | 0:Argument[] | 0:PropertyType | 0:Mandatory |

## TransferSwitchSourceType

One power source (normal/utility or emergency/generator) of an automatic transfer switch, with its availability and measurements.

Table 44 – TransferSwitchSourceType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:TransferSwitchSourceType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:BaseObjectType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | Available | 0:Boolean | 0:BaseDataVariableType | M |
| 0:HasComponent | Variable | Acceptable | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | Voltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | Frequency | 0:Double | 0:AnalogUnitType | O |
| 0:HasProperty | Variable | PhaseRotation | 0:String | 0:PropertyType | O |
| Conformance Units |  |  |  |  |  |
| GEN-TransferSwitch |  |  |  |  |  |

## AutomaticTransferSwitchType

An automatic transfer switch (ATS) that transfers a load between a normal source (utility) and an emergency source (generator).

Table 45 – AutomaticTransferSwitchType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AutomaticTransferSwitchType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:DeviceType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasAddIn | Object | Identification |  | 3:MachineIdentificationType | O |
| 0:HasComponent | Variable | Position | TransferSwitchPositionEnum | 0:BaseDataVariableType | M |
| 0:HasComponent | Variable | OperatingState | AtsOperatingStateEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | TransitionType | TransferTransitionTypeEnum | 0:BaseDataVariableType | O |
| 0:HasComponent | Object | Source1 |  | TransferSwitchSourceType | M |
| 0:HasComponent | Object | Source2 |  | TransferSwitchSourceType | M |
| 0:HasProperty | Variable | PreferredSource | 0:Byte | 0:PropertyType | O |
| 0:HasComponent | Variable | Source1Connected | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | Source2Connected | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | TransferInhibited | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasProperty | Variable | TransferInhibitReason | 0:String | 0:PropertyType | O |
| 0:HasComponent | Variable | RatedCurrent | 0:Double | 0:AnalogUnitType | O |
| 0:HasProperty | Variable | PoleCount | 0:Byte | 0:PropertyType | O |
| 0:HasComponent | Variable | ServiceEntranceRated | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | LoadCurrent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TransferCount | 0:UInt32 | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | LastTransferTime | 0:DateTime | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | EngineStartDelay | 0:Duration | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | TransferToEmergencyDelay | 0:Duration | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | RetransferToNormalDelay | 0:Duration | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | CooldownDelay | 0:Duration | 0:BaseDataVariableType | O |
| 0:HasComponent | Method | Transfer |  |  | O |
| 0:HasComponent | Method | Retransfer |  |  | O |
| 0:HasComponent | Method | InhibitTransfer |  |  | O |
| Conformance Units |  |  |  |  |  |
| GEN-TransferSwitch |  |  |  |  |  |

### Transfer

Command a transfer to the emergency source.

Signature

Transfer ();

### Retransfer

Command a retransfer to the normal source.

Signature

Retransfer ();

### InhibitTransfer

Enable or disable the transfer inhibit.

Signature

InhibitTransfer (

[in]  0:Boolean      Inhibit);

Table 46 – InhibitTransfer Method Arguments

| Argument | Description |
| --- | --- |
| Inhibit | TRUE to inhibit transfer. |

Table 47 – InhibitTransfer Method AddressSpace definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | InhibitTransfer |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | ModellingRule |
| 0:HasProperty | Variable | 0:InputArguments | 0:Argument[] | 0:PropertyType | 0:Mandatory |

## ParallelingControllerType

A paralleling / switchgear controller that synchronizes and shares load among generator sets on a common bus, and optionally parallels with the utility.

Table 48 – ParallelingControllerType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:ParallelingControllerType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 2:ComponentType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Variable | SystemState | ParallelingSystemStateEnum | 0:BaseDataVariableType | M |
| 0:HasComponent | Variable | BusVoltage | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | BusFrequency | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TotalBusRealPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TotalBusReactivePower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | SynchronizationAngle | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | SlipFrequency | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | VoltageDifference | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | FrequencyDifference | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | SyncCheckPermissive | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | DeadBus | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | LoadSharePercent | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | AvailableCapacity | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | SpinningReserve | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | GeneratorBreakerClosed | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | UtilityBreakerClosed | 0:Boolean | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | UtilityImportPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | UtilityExportPower | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Method | ConnectToBus |  |  | O |
| 0:HasComponent | Method | DisconnectFromBus |  |  | O |
| Conformance Units |  |  |  |  |  |
| GEN-Paralleling |  |  |  |  |  |

### ConnectToBus

Synchronize and close onto the common bus.

Signature

ConnectToBus ();

### DisconnectFromBus

Soft-unload and open from the common bus.

Signature

DisconnectFromBus ();

## GeneratorSystemType

A power-generation system aggregating one or more paralleled generator sets, an optional paralleling controller and transfer switches. Models integrated power systems such as data-center and healthcare plants.

Table 49 – GeneratorSystemType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorSystemType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:BaseObjectType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasComponent | Object | GeneratorSets |  | 0:FolderType | M |
| 0:HasComponent | Object | ParallelingController |  | ParallelingControllerType | O |
| 0:HasComponent | Object | TransferSwitches |  | 0:FolderType | O |
| 0:HasComponent | Variable | NumberOfGeneratorSets | 0:UInt16 | 0:BaseDataVariableType | O |
| 0:HasComponent | Variable | TotalSystemCapacity | 0:Double | 0:AnalogUnitType | O |
| 0:HasComponent | Variable | TotalSystemLoad | 0:Double | 0:AnalogUnitType | O |
| 0:HasProperty | Variable | RedundancyScheme | 0:String | 0:PropertyType | O |
| Conformance Units |  |  |  |  |  |
| GEN-System |  |  |  |  |  |

# OPC UA EventTypes

## GeneratorProtectionAlarmType

Alarm raised by a generator protection/shutdown function. Extends OffNormalAlarmType with the protection function, automatic protection action and J1939 origin. The inherited Severity field is the sole event urgency.

Table 50 – GeneratorProtectionAlarmType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorProtectionAlarmType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:OffNormalAlarmType defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | ProtectionFunction | GeneratorProtectionFunctionEnum | 0:PropertyType | M |
| 0:HasProperty | Variable | GeneratorAlarmSeverity | AlarmSeverityEnum | 0:PropertyType | O |
| 0:HasProperty | Variable | IsShutdown | 0:Boolean | 0:PropertyType | O |
| 0:HasProperty | Variable | Spn | 0:UInt32 | 0:PropertyType | O |
| 0:HasProperty | Variable | Fmi | 0:Byte | 0:PropertyType | O |
| 0:HasProperty | Variable | SubsystemName | 0:String | 0:PropertyType | O |
| 0:HasProperty | Variable | ProtectionAction | GeneratorProtectionActionEnum | 0:PropertyType | O |
| Conformance Units |  |  |  |  |  |
| GEN-Alarms |  |  |  |  |  |

# OPC UA DataTypes

## GeneratorOperatingModeEnum

Selector mode of the generator set control panel.

Table 51 – GeneratorOperatingModeEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Off | 0 | Control is off; the set will not start automatically or manually. |
| Manual | 1 | Manual/hand mode; the set runs on operator command. |
| Auto | 2 | Automatic mode; the set starts/stops on remote or utility-failure signals. |
| Test | 3 | Test mode; a commanded test run, optionally with load. |
| Exercise | 4 | Scheduled exercise/self-test run. |
| RemoteStart | 5 | Started by a remote start signal. |
| Maintenance | 6 | Maintenance/service mode; starting is inhibited or restricted. |
| Lockout | 7 | Locked out; starting is blocked until reset. |

Table 52 – GeneratorOperatingModeEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorOperatingModeEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[8] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## FuelTypeEnum

Primary fuel of the generator set.

Table 53 – FuelTypeEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Diesel | 0 |  |
| NaturalGas | 1 |  |
| Propane | 2 |  |
| LPG | 3 |  |
| Gasoline | 4 |  |
| BiFuel | 5 |  |
| DualFuel | 6 |  |
| Biodiesel | 7 |  |
| HVO | 8 |  |
| RenewableDiesel | 9 |  |
| Hydrogen | 10 |  |
| Biogas | 11 |  |
| LandfillGas | 12 |  |
| FieldGas | 13 |  |
| Syngas | 14 |  |
| Other | 15 |  |

Table 54 – FuelTypeEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:FuelTypeEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[16] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## GeneratorApplicationRatingEnum

Application/duty rating per ISO 8528 plus the data-center-continuous rating.

Table 55 – GeneratorApplicationRatingEnum Items

| Name | Value | Description |
| --- | --- | --- |
| EmergencyStandby | 0 | ESP: standby power at variable load, limited hours, no overload. |
| Prime | 1 | PRP: unlimited hours at variable load, typically 10% overload 1h/12h. |
| Continuous | 2 | COP: unlimited hours at constant load, no overload. |
| LimitedTime | 3 | LTP: limited hours per year at defined load. |
| DataCenterContinuous | 4 | DCC: continuous operation for data-center loads. |

Table 56 – GeneratorApplicationRatingEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorApplicationRatingEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[5] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## ElectricalConnectionEnum

Winding/connection configuration of the alternator output.

Table 57 – ElectricalConnectionEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Unknown | 0 |  |
| Wye | 1 |  |
| WyeSolidlyGrounded | 2 |  |
| WyeResistanceGrounded | 3 |  |
| WyeUngrounded | 4 |  |
| Delta | 5 |  |
| OpenDelta | 6 |  |
| ZigZag | 7 |  |
| SinglePhaseThreeWire | 8 |  |

Table 58 – ElectricalConnectionEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:ElectricalConnectionEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[9] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## ExcitationTypeEnum

Excitation method of the alternator.

Table 59 – ExcitationTypeEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Unknown | 0 |  |
| Shunt | 1 |  |
| PMG | 2 | Permanent Magnet Generator - independent excitation supply. |
| AREP | 3 |  |
| AuxiliaryWinding | 4 |  |
| StaticExciter | 5 |  |

Table 60 – ExcitationTypeEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:ExcitationTypeEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[6] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## CoolingMethodEnum

Primary cooling method of the engine.

Table 61 – CoolingMethodEnum Items

| Name | Value | Description |
| --- | --- | --- |
| AirCooled | 0 |  |
| LiquidCooled | 1 |  |

Table 62 – CoolingMethodEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:CoolingMethodEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[2] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## AspirationEnum

Air induction method of the engine.

Table 63 – AspirationEnum Items

| Name | Value | Description |
| --- | --- | --- |
| NaturallyAspirated | 0 |  |
| Turbocharged | 1 |  |
| TurbochargedAftercooled | 2 |  |

Table 64 – AspirationEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AspirationEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[3] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## EmissionsStandardEnum

Emissions certification standard of the engine.

Table 65 – EmissionsStandardEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Unregulated | 0 |  |
| EPATier1 | 1 |  |
| EPATier2 | 2 |  |
| EPATier3 | 3 |  |
| EPATier4Interim | 4 |  |
| EPATier4Final | 5 |  |
| EUStageIII | 6 |  |
| EUStageIV | 7 |  |
| EUStageV | 8 |  |
| Other | 9 |  |

Table 66 – EmissionsStandardEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:EmissionsStandardEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[10] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## CanBusStateEnum

State of the engine CAN bus / SAE J1939 network interface.

Table 67 – CanBusStateEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Offline | 0 |  |
| Online | 1 |  |
| ErrorWarning | 2 |  |
| ErrorPassive | 3 |  |
| BusOff | 4 |  |

Table 68 – CanBusStateEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:CanBusStateEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[5] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## TransferSwitchPositionEnum

Contact position of an automatic transfer switch.

Table 69 – TransferSwitchPositionEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Unknown | 0 |  |
| Source1 | 1 | Connected to Source 1 (normal/utility). |
| Source2 | 2 | Connected to Source 2 (emergency/generator). |
| Neutral | 3 | Center-off / neutral position. |
| InTransition | 4 |  |
| BypassSource1 | 5 |  |
| BypassSource2 | 6 |  |
| Isolated | 7 |  |

Table 70 – TransferSwitchPositionEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:TransferSwitchPositionEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[8] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## TransferTransitionTypeEnum

Transition method of an automatic transfer switch.

Table 71 – TransferTransitionTypeEnum Items

| Name | Value | Description |
| --- | --- | --- |
| OpenTransition | 0 | Break-before-make. |
| DelayedTransition | 1 | Break-before-make with center-off delay. |
| ClosedTransition | 2 | Make-before-break; momentary paralleling. |
| SoftLoadTransition | 3 | Ramped, no-break transfer while paralleled. |
| BypassIsolation | 4 |  |

Table 72 – TransferTransitionTypeEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:TransferTransitionTypeEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[5] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## AtsOperatingStateEnum

Operating state of an automatic transfer switch.

Table 73 – AtsOperatingStateEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Unknown | 0 |  |
| NormalAvailable | 1 |  |
| EmergencyAvailable | 2 |  |
| NormalConnected | 3 |  |
| EmergencyConnected | 4 |  |
| TransferPending | 5 |  |
| Transferring | 6 |  |
| RetransferPending | 7 |  |
| Exercising | 8 |  |
| Test | 9 |  |
| Faulted | 10 |  |
| Bypassed | 11 |  |
| Isolated | 12 |  |

Table 74 – AtsOperatingStateEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AtsOperatingStateEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[13] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## AlarmSeverityEnum

Severity class of a generator protection event.

Table 75 – AlarmSeverityEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Info | 0 |  |
| Warning | 1 |  |
| Derate | 2 | The set continues to run at reduced output. |
| Shutdown | 3 | The engine is shut down. |
| ElectricalTrip | 4 | The generator breaker is tripped. |
| Lockout | 5 | The set is locked out and requires manual reset. |
| EmergencyStop | 6 |  |

Table 76 – AlarmSeverityEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AlarmSeverityEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[7] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## GeneratorProtectionFunctionEnum

Protection / fault function that raised a generator alarm.

Table 77 – GeneratorProtectionFunctionEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Other | 0 |  |
| LowOilPressure | 1 |  |
| HighOilTemperature | 2 |  |
| HighCoolantTemperature | 3 |  |
| LowCoolantTemperature | 4 |  |
| LowCoolantLevel | 5 |  |
| HighCoolantPressure | 6 |  |
| Overspeed | 7 |  |
| Underspeed | 8 |  |
| Overcrank | 9 | Fail to start within the crank limit. |
| FailToCrank | 10 |  |
| StarterFailure | 11 |  |
| LowFuelLevel | 12 |  |
| CriticalLowFuel | 13 |  |
| FuelLeak | 14 |  |
| LowFuelPressure | 15 |  |
| HighFuelPressure | 16 |  |
| WaterInFuel | 17 |  |
| FuelFilterRestriction | 18 |  |
| AirFilterRestriction | 19 |  |
| HighExhaustTemperature | 20 |  |
| TurbochargerFault | 21 |  |
| EcuFault | 22 |  |
| EngineDerate | 23 |  |
| Overvoltage | 24 |  |
| Undervoltage | 25 |  |
| Overfrequency | 26 |  |
| Underfrequency | 27 |  |
| Overload | 28 |  |
| Overcurrent | 29 |  |
| ShortCircuit | 30 |  |
| GroundFault | 31 |  |
| PhaseLoss | 32 |  |
| PhaseReversal | 33 |  |
| VoltageImbalance | 34 |  |
| CurrentImbalance | 35 |  |
| ReversePower | 36 |  |
| LossOfExcitation | 37 |  |
| Overexcitation | 38 |  |
| Underexcitation | 39 |  |
| AvrFault | 40 |  |
| HighWindingTemperature | 41 |  |
| HighBearingTemperature | 42 |  |
| LowBatteryVoltage | 43 |  |
| HighBatteryVoltage | 44 |  |
| BatteryChargerFailure | 45 |  |
| WeakBattery | 46 |  |
| ControllerFault | 47 |  |
| CommunicationLost | 48 |  |
| SensorFailure | 49 |  |
| EmergencyStop | 50 |  |
| DefLevelLow | 51 |  |
| DefQualityPoor | 52 |  |
| DpfSootHigh | 53 |  |
| RegenerationRequired | 54 |  |
| AftertreatmentFault | 55 |  |
| EnclosureHighTemperature | 56 |  |
| DoorOpen | 57 |  |
| FuelBasinLeak | 58 |  |
| RadiatorFanFailure | 59 |  |
| JacketWaterHeaterFailure | 60 |  |
| AtsFailedToTransfer | 61 |  |
| BreakerFailedToClose | 62 |  |
| SynchronizationFailure | 63 |  |

Table 78 – GeneratorProtectionFunctionEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorProtectionFunctionEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[64] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## ParallelingSystemStateEnum

Operating state of a paralleling / switchgear system.

Table 79 – ParallelingSystemStateEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Off | 0 |  |
| Standby | 1 |  |
| StartSequence | 2 |  |
| DeadBusClose | 3 |  |
| Synchronizing | 4 |  |
| Paralleling | 5 |  |
| LoadSharing | 6 |  |
| LoadDemand | 7 |  |
| UtilityParallel | 8 |  |
| PeakShaving | 9 |  |
| BaseLoad | 10 |  |
| LoadShed | 11 |  |
| SoftUnload | 12 |  |
| Cooldown | 13 |  |
| Faulted | 14 |  |
| EmergencyStop | 15 |  |
| MaintenanceBypass | 16 |  |

Table 80 – ParallelingSystemStateEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:ParallelingSystemStateEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[17] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## AftertreatmentStateEnum

State of the exhaust aftertreatment system.

Table 81 – AftertreatmentStateEnum Items

| Name | Value | Description |
| --- | --- | --- |
| NotEquipped | 0 |  |
| Normal | 1 |  |
| PassiveRegen | 2 |  |
| ActiveRegen | 3 |  |
| RegenInhibited | 4 |  |
| RegenRequired | 5 |  |
| DerateActive | 6 |  |
| Faulted | 7 |  |

Table 82 – AftertreatmentStateEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:AftertreatmentStateEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[8] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## J1939LampStatusEnum

SAE J1939 DM1 diagnostic lamp status (lamp state plus flash rate).

Table 83 – J1939LampStatusEnum Items

| Name | Value | Description |
| --- | --- | --- |
| Off | 0 | The lamp is off. |
| On | 1 | The lamp is on (steady). |
| SlowFlash | 2 | The lamp is flashing slowly. |
| FastFlash | 3 | The lamp is flashing fast. |
| NotAvailable | 4 | The lamp status is not available. |

Table 84 – J1939LampStatusEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:J1939LampStatusEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[5] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## DiagnosticTroubleCodeType

A SAE J1939 diagnostic trouble code (DTC) reported by an engine ECU.

Table 85 – DiagnosticTroubleCodeType Items

| Name | Type | Cardinality | Description |
| --- | --- | --- | --- |
| Spn | 0:UInt32 | 1 | Suspect Parameter Number identifying the faulty subsystem. |
| Fmi | 0:Byte | 1 | Failure Mode Identifier describing the type of failure. |
| OccurrenceCount | 0:Byte | 1 | Number of times the fault has become active. |
| ConversionMethod | 0:Boolean | 1 | J1939 SPN conversion method flag. |
| Active | 0:Boolean | 1 | TRUE while the fault is currently active (DM1). |
| SourceAddress | 0:Byte | 1 | J1939 source address of the ECU that reported the code. |
| SourceName | 0:String | 1 | Name of the ECU/controller that reported the code. |
| Severity | AlarmSeverityEnum | 1 | Severity classification of the fault. |
| Description | 0:String | 1 | Human-readable description of the fault. |

Table 86 – DiagnosticTroubleCodeType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:DiagnosticTroubleCodeType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Structure defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasEncoding | Object | Default Binary |  | 0:DataTypeEncodingType |  |
| 0:HasEncoding | Object | Default XML |  | 0:DataTypeEncodingType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## GeneratorProtectionActionEnum

Automatic response requested by a generator protection function. This is independent of the standard Part 9 event Severity.

Table 87 – GeneratorProtectionActionEnum Items

| Name | Value | Description |
| --- | --- | --- |
| NoAutomaticAction | 0 | No automatic response is requested. |
| Warning | 1 | Notify an operator without changing generator operation. |
| Derate | 2 | Continue to run at reduced output. |
| Shutdown | 3 | Shut down the prime mover. |
| ElectricalTrip | 4 | Trip the generator breaker. |
| Lockout | 5 | Prevent restart until a manual reset. |
| EmergencyStop | 6 | Perform an immediate emergency stop. |

Table 88 – GeneratorProtectionActionEnum definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:GeneratorProtectionActionEnum |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Enumeration defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasProperty | Variable | EnumStrings | 0:LocalizedText[7] | 0:PropertyType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

## DiagnosticTroubleCodeDataType

A SAE J1939 diagnostic trouble code (DTC) reported by an engine ECU.

Table 89 – DiagnosticTroubleCodeDataType Items

| Name | Type | Cardinality | Description |
| --- | --- | --- | --- |
| Spn | 0:UInt32 | 1 | Suspect Parameter Number identifying the faulty subsystem. |
| Fmi | 0:Byte | 1 | Failure Mode Identifier describing the type of failure. |
| OccurrenceCount | 0:Byte | 1 | Number of times the fault has become active. |
| ConversionMethod | 0:Boolean | 1 | J1939 SPN conversion method flag. |
| Active | 0:Boolean | 1 | TRUE while the fault is currently active (DM1). |
| SourceAddress | 0:Byte | 1 | J1939 source address of the ECU that reported the code. |
| SourceName | 0:String | 1 | Name of the ECU/controller that reported the code. |
| ProtectionAction | GeneratorProtectionActionEnum | 0..1 | Automatic generator response associated with the fault, when known. Event urgency is carried by the standard Part 9 Severity field when the DTC raises an alarm. |
| Description | 0:String | 1 | Human-readable description of the fault. |

Table 90 – DiagnosticTroubleCodeDataType definition

| Attribute | Value |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BrowseName | 1:DiagnosticTroubleCodeDataType |  |  |  |  |
| IsAbstract | False |  |  |  |  |
| References | NodeClass | BrowseName | DataType | TypeDefinition | Other |
| Subtype of the 0:Structure defined in OPC 10000-5, i.e. inheriting the InstanceDeclarations of that Node. |  |  |  |  |  |
| 0:HasEncoding | Object | Default Binary |  | 0:DataTypeEncodingType |  |
| 0:HasEncoding | Object | Default XML |  | 0:DataTypeEncodingType |  |
| Conformance Units |  |  |  |  |  |
| GEN-GeneratorSet |  |  |  |  |  |

# Profiles and conformance units

A server implementing this specification should implement the GeneratorSetType and its mandatory content. Support for individual subsystems (fuel, cooling, lubrication, starting, aftertreatment), for AutomaticTransferSwitchType, ParallelingControllerType and GeneratorSystemType, and for the control methods is optional and should be advertised through appropriate profiles/facets. Instances of GeneratorSetType should be made discoverable by organising them under the Machinery Machines folder, as recommended by OPC 40001‑1.

Mandatory children inherited from the chosen base types are not re‑declared in this NodeSet, but conforming instances must still expose them. In particular: the DI DeviceType nameplate (Manufacturer, Model, SerialNumber, HardwareRevision, SoftwareRevision, DeviceRevision, DeviceManual, RevisionCounter); the FiniteStateMachineType CurrentState on OperatingState; the AnalogUnitType EngineeringUnits on every measured value (this specification pre‑populates it with a default unit); and the OffNormalAlarmType / AcknowledgeableConditionType condition state (EnabledState, ActiveState, AckedState, NormalState). Optional but recommended children — such as the FiniteStateMachineType LastTransition and the AnalogUnitType EURange / InstrumentRange — should be provided where the information is available.

Conformance is composed from independently implementable conformance units (CUs), one per subsystem. Only GEN-GeneratorSet is mandatory; every other unit may be claimed on its own.

Table 91 – Profiles and conformance units

| Conformance unit | Requires |
| --- | --- |
| GEN-GeneratorSet | Mandatory. GeneratorSetType with its mandatory content, and the enumerations and structures the model is written in. |
| GEN-Components | The engine, alternator, alternator phase and support subsystems (fuel, cooling, lubrication, starting, aftertreatment). |
| GEN-Identification | The generator-set nameplate beyond the inherited DI nameplate. |
| GEN-StateMachine | GeneratorStateMachineType, its states and transitions, and the operating modes. |
| GEN-Rating | GeneratorRatingType and the rating set of a generator set. |
| GEN-Alarms | The protection and alarm conditions and their condition state. |
| GEN-CANbus | The CAN bus / SAE J1939 interface of the engine. |
| GEN-TransferSwitch | AutomaticTransferSwitchType and its transfer behaviour. |
| GEN-Paralleling | ParallelingControllerType and the paralleling and load-sharing behaviour. |
| GEN-System | GeneratorSystemType, the aggregate of several generator sets. |

Profiles. Generator Set Server = GEN-GeneratorSet + GEN-Components + GEN-Identification + GEN-StateMachine + GEN-Rating. Generator Set Server with alarms adds GEN-Alarms and GEN-CANbus. Generator Plant Server adds GEN-TransferSwitch, GEN-Paralleling and GEN-System.

# Namespaces

## Namespace metadata

The namespace metadata provide standardized information about the elements of this namespace, which an aggregating Server relies on. All Nodes defined by this document are static: they are identical in every Server, including the Value Attribute.

The information is provided as an Object of type NamespaceMetadataType, a component of the Namespaces Object of the Server Object. The NamespaceMetadataType ObjectType and its Properties are defined in OPC 10000-5. The same version information is carried by the ModelTableEntry of the UANodeSet XML file.

Table 92 – NamespaceMetadata Object for this document

| Property | DataType | Value |
| --- | --- | --- |
| NamespaceUri | String | http://opcfoundation.org/UA/Generators/ |
| NamespaceVersion | String | 1.2.0 |
| NamespacePublicationDate | DateTime | 2026-08-11 |
| IsNamespaceSubset | Boolean | False |
| StaticNodeIdTypes | IdType[] | 0 (Numeric) |
| StaticNumericNodeIdRange | NumericRange[] | 1001:6404 |
| StaticStringNodeIdPattern | String | -- |

The IsNamespaceSubset Property is False because the UANodeSet XML file contains the complete namespace. A Server exposing only a subset sets it to True.

## Handling of OPC UA namespaces

Namespaces are used by OPC UA to create unique identifiers across different naming authorities. The NodeId and BrowseName Attributes are identifiers. A Node in the AddressSpace is unambiguously identified by its NodeId; a BrowseName is not unique and is used to build a browse path or to name a standard Property.

Table 93 – Namespaces used in an OpenUSD Server

| NamespaceURI | Description |
| --- | --- |
| http://opcfoundation.org/UA/ | Namespace for NodeIds and BrowseNames defined in the OPC UA specification (OPC 10000-3, OPC 10000-5). |
| Local Server URI | Namespace for Nodes defined in the local Server. This namespace shall have index 1. |
| http://opcfoundation.org/UA/xRegistry/ | Namespace of the RequiredModel that carries the abstract registry base types this document extends. |
| http://opcfoundation.org/UA/Generators/ | Namespace for NodeIds and BrowseNames defined in this document. |
| Vendor specific types | A Server may provide vendor-specific types derived from the types defined in this document, in one or more additional namespaces. |

The following table lists the namespaces and their indexes used for BrowseNames in this document. The default namespace of this document is not listed, because every BrowseName without a prefix uses it.

Table 94 – Namespaces used in this document

| NamespaceURI | Namespace Index | Example |
| --- | --- | --- |
| http://opcfoundation.org/UA/ | 0 | 0:EngineeringUnits |
| http://opcfoundation.org/UA/xRegistry/ | 1 | 1:ResourceType |

(normative) 

Generators namespace and mappings

NodeSet and supplementary files for Generators Information Model

An Information Model is formally defined in an XML file called a NodeSet This file conforms to the standard syntax defined in the Annex “Information Model XML Schema” OPC 10000-6, OPC Unified Architecture - Part 6: Mappings. It can be read and processed by a computer program.

An Information Model is identified by a URI – the so-called NamespaceUri.

A NamespaceUri follows one of these conventions:

http://opcfoundation.org/UA/GEN/

tag:opcfoundation.org,yyyy-MM:UA:GEN

Where GEN is described in 10 and yyyy-MM is the date when the NamespaceUri was first published. NamespaceUris are not network accessible URLs and the text should not suggest they are. The tag URI syntax allows authors to choose a URI that cannot be used as URL by mistake. Note that the date in the tag syntax is not the same as the PublicationDate for the NodeSet. It is set once when the URI is created and never changed.

The Online Reference provides a summary page for every NamespaceUri of released Information Models which has the form:

https://reference.opcfoundation.org/nodesets?u=http://opcfoundation.org/UA/Generators/

The Generators Information Model is identified by the following URI:

http://opcfoundation.org/UA/GEN/

Documentation for the NamespaceUri can be found here.

“here” is a hyperlink to the summary page of the Online Reference.

In the hyperlink, the http://opcfoundation.org/UA/Generators/ has to be replaced with the concrete URI for this specification.

The NodeSet associated with this version of specification can be found here:

https://reference.opcfoundation.org/nodesets/?u=http://opcfoundation.org/UA/Generators/&v=1.2.0&i=1

The NodeSet associated with the latest version of the specification can be found here:

https://reference.opcfoundation.org/nodesets/?u=http://opcfoundation.org/UA/Generators/&i=1

http://opcfoundation.org/UA/Generators/ is the NamespaceUri for the Information Model.

The 1.2.0 is the string in the NamespaceVersion from the Namespace Metadata (see 11.1). This value is also the value of the Version attribute in the NodeSet.

Supplementary files for the Generators Information Model can be found here:

https://reference.opcfoundation.org/nodesets/?u=http://opcfoundation.org/UA/Generators/&v=1.2.0&i=2

The files associated with the latest version of the specification can be found here:

https://reference.opcfoundation.org/nodesets/?u=http://opcfoundation.org/UA/Generators/&i=2

Supplementary files should be provided when appropriate (i.e., IRDI NodeSets or examples)

File Names

NodeIds: 	Opc.Ua.GEN.NodeIds.csv

NodeSet: 	Opc.Ua.GEN.NodeSet2.xml;

Any other files should have a prefix that provides context when the file is downloaded in a browser.

When DataTypes are defined in the NodeSet:

Opc.ua.GEN.Types.xsd –

The XML schema for the DataTypes defined by the specification;

Opc.ua.GEN.Types.bsd –

The OPC Binary schema for the DataTypes defined by the specification;

In case there is the need to reference individual files the following syntax should be added to the template:

https://reference.opcfoundation.org/files/<file>?u=<namespaceUri>&v=<version>
https://reference.opcfoundation.org/files/<file>?u=<namespaceUri>

for example:

https://reference.opcfoundation.org/files/StatusCode.csv?u=http://opcfoundation.org/UA/&v=1.05.02
https://reference.opcfoundation.org/files/StatusCode.csv?u=http://opcfoundation.org/UA/
https://reference.opcfoundation.org/files/Opc.Ua.Types.xsd?u=http://opcfoundation.org/UA/&v=1.05.02
https://reference.opcfoundation.org/files/Opc.Ua.Types.xsd?u=http://opcfoundation.org/UA/

Capability identifier

ServerCapabilityIdentifiers are defined in OPC 10000-12, OPC Unified Architecture - Part 12: Discovery and Global Services. They can be used for features, like certain information models, which are likely to be useful during the discovery process. The identifiers shall be short because of length restrictions for fields used in the mDNS specification.

The identifier shall be up to 6 characters. It is recommended to use the GEN introduced in the guideline, at the beginning of clause 10 if that meets the requirement of up to 6 characters.

Note, that such identifiers are not required. If not needed, this Annex section shall be deleted.

The capability identifier for this document shall be:

GEN

Node reference

The following table lists every Node this document defines, with the provisional NodeId assigned by the generator. It is generated from the UANodeSet and is informative for navigation; the UANodeSet is authoritative.

Table 95 – Nodes defined by this document

| NodeId | BrowseName | NodeClass | Description |
| --- | --- | --- | --- |
| ns=1;i=3001 | GeneratorOperatingModeEnum | DataType | Selector mode of the generator set control panel. |
| ns=1;i=3901 | EnumStrings | Variable |  |
| ns=1;i=3002 | FuelTypeEnum | DataType | Primary fuel of the generator set. |
| ns=1;i=3902 | EnumStrings | Variable |  |
| ns=1;i=3003 | GeneratorApplicationRatingEnum | DataType | Application/duty rating per ISO 8528 plus the data-center-continuous rating. |
| ns=1;i=3903 | EnumStrings | Variable |  |
| ns=1;i=3004 | ElectricalConnectionEnum | DataType | Winding/connection configuration of the alternator output. |
| ns=1;i=3904 | EnumStrings | Variable |  |
| ns=1;i=3005 | ExcitationTypeEnum | DataType | Excitation method of the alternator. |
| ns=1;i=3905 | EnumStrings | Variable |  |
| ns=1;i=3006 | CoolingMethodEnum | DataType | Primary cooling method of the engine. |
| ns=1;i=3906 | EnumStrings | Variable |  |
| ns=1;i=3007 | AspirationEnum | DataType | Air induction method of the engine. |
| ns=1;i=3907 | EnumStrings | Variable |  |
| ns=1;i=3008 | EmissionsStandardEnum | DataType | Emissions certification standard of the engine. |
| ns=1;i=3908 | EnumStrings | Variable |  |
| ns=1;i=3009 | CanBusStateEnum | DataType | State of the engine CAN bus / SAE J1939 network interface. |
| ns=1;i=3909 | EnumStrings | Variable |  |
| ns=1;i=3010 | TransferSwitchPositionEnum | DataType | Contact position of an automatic transfer switch. |
| ns=1;i=3910 | EnumStrings | Variable |  |
| ns=1;i=3011 | TransferTransitionTypeEnum | DataType | Transition method of an automatic transfer switch. |
| ns=1;i=3911 | EnumStrings | Variable |  |
| ns=1;i=3012 | AtsOperatingStateEnum | DataType | Operating state of an automatic transfer switch. |
| ns=1;i=3912 | EnumStrings | Variable |  |
| ns=1;i=3013 | AlarmSeverityEnum | DataType | Severity class of a generator protection event. |
| ns=1;i=3913 | EnumStrings | Variable |  |
| ns=1;i=3014 | GeneratorProtectionFunctionEnum | DataType | Protection / fault function that raised a generator alarm. |
| ns=1;i=3914 | EnumStrings | Variable |  |
| ns=1;i=3015 | ParallelingSystemStateEnum | DataType | Operating state of a paralleling / switchgear system. |
| ns=1;i=3915 | EnumStrings | Variable |  |
| ns=1;i=3016 | AftertreatmentStateEnum | DataType | State of the exhaust aftertreatment system. |
| ns=1;i=3916 | EnumStrings | Variable |  |
| ns=1;i=3017 | J1939LampStatusEnum | DataType | SAE J1939 DM1 diagnostic lamp status (lamp state plus flash rate). |
| ns=1;i=3917 | EnumStrings | Variable |  |
| ns=1;i=3050 | DiagnosticTroubleCodeType | DataType | A SAE J1939 diagnostic trouble code (DTC) reported by an engine ECU. |
| ns=1;i=6001 | Default Binary | Object |  |
| ns=1;i=6002 | Default XML | Object |  |
| ns=1;i=1016 | GeneratorIdentificationType | ObjectType | Identification and nameplate of a generator set. Extends the Machinery MachineIdentificationType with generator-specific nameplate data. |
| ns=1;i=6003 | SpecificationNumber | Variable | Vendor build/specification code that identifies the exact configuration. |
| ns=1;i=6004 | ProductFamily | Variable | Vendor product family or series to which the set belongs. |
| ns=1;i=6005 | EngineModel | Variable | Model designation of the prime-mover engine. |
| ns=1;i=6006 | EngineSerialNumber | Variable | Serial number of the prime-mover engine. |
| ns=1;i=6007 | AlternatorModel | Variable | Model designation of the alternator. |
| ns=1;i=6008 | AlternatorSerialNumber | Variable | Serial number of the alternator. |
| ns=1;i=6009 | ControllerModel | Variable | Model designation of the control panel. |
| ns=1;i=6010 | FuelType | Variable | Primary fuel of the set. |
| ns=1;i=6011 | EmissionsStandard | Variable | Emissions certification standard. |
| ns=1;i=6012 | RatedRealPower | Variable | Nameplate rated real power. EngineeringUnits: kW. |
| ns=1;i=6013 | EngineeringUnits | Variable |  |
| ns=1;i=6014 | RatedApparentPower | Variable | Nameplate rated apparent power. EngineeringUnits: kVA. |
| ns=1;i=6015 | EngineeringUnits | Variable |  |
| ns=1;i=6016 | RatedVoltage | Variable | Nameplate rated line-to-line voltage. EngineeringUnits: V. |
| ns=1;i=6017 | EngineeringUnits | Variable |  |
| ns=1;i=6018 | RatedFrequency | Variable | Nameplate rated frequency. EngineeringUnits: Hz. |
| ns=1;i=6019 | EngineeringUnits | Variable |  |
| ns=1;i=6020 | SoundRatingAt7m | Variable | Sound pressure level at 7 m (23 ft) in dB(A). |
| ns=1;i=1011 | GeneratorStateMachineType | ObjectType | Finite state machine describing the operating state of a generator set: Off, Ready, Starting, Warmup, Running, Loaded, Synchronizing, Paralleled, Cooldown, Stopping, Fault and EmergencyStopped. |
| ns=1;i=6021 | Off | Object | State 'Off' of the generator set operating state machine. |
| ns=1;i=6022 | StateNumber | Variable |  |
| ns=1;i=6023 | Ready | Object | State 'Ready' of the generator set operating state machine. |
| ns=1;i=6024 | StateNumber | Variable |  |
| ns=1;i=6025 | Starting | Object | State 'Starting' of the generator set operating state machine. |
| ns=1;i=6026 | StateNumber | Variable |  |
| ns=1;i=6027 | Warmup | Object | State 'Warmup' of the generator set operating state machine. |
| ns=1;i=6028 | StateNumber | Variable |  |
| ns=1;i=6029 | Running | Object | State 'Running' of the generator set operating state machine. |
| ns=1;i=6030 | StateNumber | Variable |  |
| ns=1;i=6031 | Loaded | Object | State 'Loaded' of the generator set operating state machine. |
| ns=1;i=6032 | StateNumber | Variable |  |
| ns=1;i=6033 | Synchronizing | Object | State 'Synchronizing' of the generator set operating state machine. |
| ns=1;i=6034 | StateNumber | Variable |  |
| ns=1;i=6035 | Paralleled | Object | State 'Paralleled' of the generator set operating state machine. |
| ns=1;i=6036 | StateNumber | Variable |  |
| ns=1;i=6037 | Cooldown | Object | State 'Cooldown' of the generator set operating state machine. |
| ns=1;i=6038 | StateNumber | Variable |  |
| ns=1;i=6039 | Stopping | Object | State 'Stopping' of the generator set operating state machine. |
| ns=1;i=6040 | StateNumber | Variable |  |
| ns=1;i=6041 | Fault | Object | State 'Fault' of the generator set operating state machine. |
| ns=1;i=6042 | StateNumber | Variable |  |
| ns=1;i=6043 | EmergencyStopped | Object | State 'EmergencyStopped' of the generator set operating state machine. |
| ns=1;i=6044 | StateNumber | Variable |  |
| ns=1;i=6045 | OffToReady | Object | Transition 'OffToReady'. |
| ns=1;i=6046 | TransitionNumber | Variable |  |
| ns=1;i=6047 | ReadyToStarting | Object | Transition 'ReadyToStarting'. |
| ns=1;i=6048 | TransitionNumber | Variable |  |
| ns=1;i=6049 | ReadyToOff | Object | Transition 'ReadyToOff'. |
| ns=1;i=6050 | TransitionNumber | Variable |  |
| ns=1;i=6051 | StartingToWarmup | Object | Transition 'StartingToWarmup'. |
| ns=1;i=6052 | TransitionNumber | Variable |  |
| ns=1;i=6053 | StartingToFault | Object | Transition 'StartingToFault'. |
| ns=1;i=6054 | TransitionNumber | Variable |  |
| ns=1;i=6055 | WarmupToRunning | Object | Transition 'WarmupToRunning'. |
| ns=1;i=6056 | TransitionNumber | Variable |  |
| ns=1;i=6057 | RunningToLoaded | Object | Transition 'RunningToLoaded'. |
| ns=1;i=6058 | TransitionNumber | Variable |  |
| ns=1;i=6059 | RunningToSynchronizing | Object | Transition 'RunningToSynchronizing'. |
| ns=1;i=6060 | TransitionNumber | Variable |  |
| ns=1;i=6061 | SynchronizingToParalleled | Object | Transition 'SynchronizingToParalleled'. |
| ns=1;i=6062 | TransitionNumber | Variable |  |
| ns=1;i=6063 | SynchronizingToRunning | Object | Transition 'SynchronizingToRunning'. |
| ns=1;i=6064 | TransitionNumber | Variable |  |
| ns=1;i=6065 | ParalleledToLoaded | Object | Transition 'ParalleledToLoaded'. |
| ns=1;i=6066 | TransitionNumber | Variable |  |
| ns=1;i=6067 | LoadedToCooldown | Object | Transition 'LoadedToCooldown'. |
| ns=1;i=6068 | TransitionNumber | Variable |  |
| ns=1;i=6069 | RunningToCooldown | Object | Transition 'RunningToCooldown'. |
| ns=1;i=6070 | TransitionNumber | Variable |  |
| ns=1;i=6071 | CooldownToStopping | Object | Transition 'CooldownToStopping'. |
| ns=1;i=6072 | TransitionNumber | Variable |  |
| ns=1;i=6073 | StoppingToOff | Object | Transition 'StoppingToOff'. |
| ns=1;i=6074 | TransitionNumber | Variable |  |
| ns=1;i=6075 | RunningToFault | Object | Transition 'RunningToFault'. |
| ns=1;i=6076 | TransitionNumber | Variable |  |
| ns=1;i=6077 | LoadedToFault | Object | Transition 'LoadedToFault'. |
| ns=1;i=6078 | TransitionNumber | Variable |  |
| ns=1;i=6079 | ParalleledToFault | Object | Transition 'ParalleledToFault'. |
| ns=1;i=6080 | TransitionNumber | Variable |  |
| ns=1;i=6081 | FaultToOff | Object | Transition 'FaultToOff'. |
| ns=1;i=6082 | TransitionNumber | Variable |  |
| ns=1;i=6083 | RunningToEmergencyStopped | Object | Transition 'RunningToEmergencyStopped'. |
| ns=1;i=6084 | TransitionNumber | Variable |  |
| ns=1;i=6085 | LoadedToEmergencyStopped | Object | Transition 'LoadedToEmergencyStopped'. |
| ns=1;i=6086 | TransitionNumber | Variable |  |
| ns=1;i=6087 | ParalleledToEmergencyStopped | Object | Transition 'ParalleledToEmergencyStopped'. |
| ns=1;i=6088 | TransitionNumber | Variable |  |
| ns=1;i=6089 | EmergencyStoppedToOff | Object | Transition 'EmergencyStoppedToOff'. |
| ns=1;i=6090 | TransitionNumber | Variable |  |
| ns=1;i=1010 | J1939DiagnosticInterfaceType | ObjectType | The engine CAN bus / SAE J1939 diagnostic interface. Surfaces the network connection parameters, J1939 lamp status and active/previously-active diagnostic trouble codes reported by the engine ECU. |
| ns=1;i=6091 | ProtocolName | Variable | Name of the diagnostic protocol, e.g. 'SAE J1939'. |
| ns=1;i=6092 | NetworkName | Variable | Name/identifier of the CAN network (e.g. CAN0). |
| ns=1;i=6093 | SourceAddress | Variable | J1939 source address of the engine ECU. |
| ns=1;i=6094 | Baudrate | Variable | CAN bit rate in bit/s (typically 250000 or 500000). |
| ns=1;i=6095 | BusState | Variable | State of the CAN bus interface. |
| ns=1;i=6096 | AmberWarningLamp | Variable | J1939 DM1 amber warning lamp status. |
| ns=1;i=6097 | RedStopLamp | Variable | J1939 DM1 red stop lamp status. |
| ns=1;i=6098 | MalfunctionIndicatorLamp | Variable | J1939 DM1 malfunction indicator lamp status. |
| ns=1;i=6099 | ProtectLamp | Variable | J1939 DM1 protect lamp status. |
| ns=1;i=6100 | ActiveDiagnosticTroubleCodes | Variable | Currently active DTCs (J1939 DM1). |
| ns=1;i=6101 | PreviouslyActiveDiagnosticTroubleCodes | Variable | Previously active DTCs (J1939 DM2). |
| ns=1;i=6102 | ClearPreviouslyActiveDtcs | Method | Clear previously active diagnostic trouble codes (J1939 DM3/DM11). |
| ns=1;i=1018 | ExhaustAftertreatmentType | ObjectType | Exhaust aftertreatment subsystem (DPF/SCR/DEF) for Tier 4 / Stage V engines. |
| ns=1;i=6103 | AftertreatmentState | Variable | State of the aftertreatment system. |
| ns=1;i=6104 | DefLevel | Variable | Diesel Exhaust Fluid tank level. SAE J1939 SPN 1761. EngineeringUnits: %. |
| ns=1;i=6105 | EngineeringUnits | Variable |  |
| ns=1;i=6106 | DefTemperature | Variable | DEF tank temperature. SAE J1939 SPN 3031. EngineeringUnits: degC. |
| ns=1;i=6107 | EngineeringUnits | Variable |  |
| ns=1;i=6108 | DefQuality | Variable | DEF concentration/quality. SAE J1939 SPN 3364. EngineeringUnits: %. |
| ns=1;i=6109 | EngineeringUnits | Variable |  |
| ns=1;i=6110 | DpfSootLoad | Variable | Diesel particulate filter soot load. SAE J1939 SPN 3719. EngineeringUnits: %. |
| ns=1;i=6111 | EngineeringUnits | Variable |  |
| ns=1;i=6112 | DpfAshLoad | Variable | Diesel particulate filter ash load. SAE J1939 SPN 3720. EngineeringUnits: %. |
| ns=1;i=6113 | EngineeringUnits | Variable |  |
| ns=1;i=6114 | ExhaustGasTemperature | Variable | Exhaust gas temperature. SAE J1939 SPN 173. EngineeringUnits: degC. |
| ns=1;i=6115 | EngineeringUnits | Variable |  |
| ns=1;i=6116 | RegenerationRequired | Variable | A DPF regeneration is required. |
| ns=1;i=6117 | RegenerationInhibited | Variable | DPF regeneration is currently inhibited. |
| ns=1;i=6118 | InitiateRegeneration | Method | Request a manual DPF regeneration. |
| ns=1;i=6119 | InhibitRegeneration | Method | Enable or disable the inhibit of automatic regeneration. |
| ns=1;i=6120 | InputArguments | Variable |  |
| ns=1;i=1002 | EngineType | ObjectType | The prime-mover engine of a generator set. Exposes engine telemetry, typically obtained over the CAN bus / SAE J1939 interface, and identification. |
| ns=1;i=6121 | Speed | Variable | Engine speed. SAE J1939 SPN 190. EngineeringUnits: rpm. |
| ns=1;i=6122 | EngineeringUnits | Variable |  |
| ns=1;i=6123 | PercentLoad | Variable | Engine percent load at current speed. SAE J1939 SPN 92. EngineeringUnits: %. |
| ns=1;i=6124 | EngineeringUnits | Variable |  |
| ns=1;i=6125 | PercentTorque | Variable | Actual engine percent torque. SAE J1939 SPN 513. EngineeringUnits: %. |
| ns=1;i=6126 | EngineeringUnits | Variable |  |
| ns=1;i=6127 | OilPressure | Variable | Engine oil pressure. SAE J1939 SPN 100. EngineeringUnits: kPa. |
| ns=1;i=6128 | EngineeringUnits | Variable |  |
| ns=1;i=6129 | OilTemperature | Variable | Engine oil temperature. SAE J1939 SPN 175. EngineeringUnits: degC. |
| ns=1;i=6130 | EngineeringUnits | Variable |  |
| ns=1;i=6131 | CoolantTemperature | Variable | Engine coolant temperature. SAE J1939 SPN 110. EngineeringUnits: degC. |
| ns=1;i=6132 | EngineeringUnits | Variable |  |
| ns=1;i=6133 | CoolantPressure | Variable | Engine coolant pressure. SAE J1939 SPN 109. EngineeringUnits: kPa. |
| ns=1;i=6134 | EngineeringUnits | Variable |  |
| ns=1;i=6135 | FuelRate | Variable | Engine fuel consumption rate. SAE J1939 SPN 183. EngineeringUnits: L/h. |
| ns=1;i=6136 | EngineeringUnits | Variable |  |
| ns=1;i=6137 | FuelTemperature | Variable | Engine fuel temperature. SAE J1939 SPN 174. EngineeringUnits: degC. |
| ns=1;i=6138 | EngineeringUnits | Variable |  |
| ns=1;i=6139 | IntakeManifoldPressure | Variable | Intake manifold (boost) pressure. SAE J1939 SPN 102. EngineeringUnits: kPa. |
| ns=1;i=6140 | EngineeringUnits | Variable |  |
| ns=1;i=6141 | IntakeManifoldTemperature | Variable | Intake manifold temperature. SAE J1939 SPN 105. EngineeringUnits: degC. |
| ns=1;i=6142 | EngineeringUnits | Variable |  |
| ns=1;i=6143 | ExhaustGasTemperature | Variable | Exhaust gas temperature. SAE J1939 SPN 173. EngineeringUnits: degC. |
| ns=1;i=6144 | EngineeringUnits | Variable |  |
| ns=1;i=6145 | BarometricPressure | Variable | Ambient barometric pressure. SAE J1939 SPN 108. EngineeringUnits: kPa. |
| ns=1;i=6146 | EngineeringUnits | Variable |  |
| ns=1;i=6147 | EngineHours | Variable | Total engine run hours. SAE J1939 SPN 247. EngineeringUnits: h. |
| ns=1;i=6148 | EngineeringUnits | Variable |  |
| ns=1;i=6149 | NumberOfStarts | Variable | Total number of engine start attempts. |
| ns=1;i=6150 | Aspiration | Variable | Air induction method of the engine. |
| ns=1;i=6151 | Displacement | Variable | Engine displacement. EngineeringUnits: l. |
| ns=1;i=6152 | EngineeringUnits | Variable |  |
| ns=1;i=6153 | CylinderCount | Variable | Number of cylinders. |
| ns=1;i=6154 | RatedSpeed | Variable | Rated (synchronous) engine speed, e.g. 1500 or 1800 rpm. EngineeringUnits: rpm. |
| ns=1;i=6155 | EngineeringUnits | Variable |  |
| ns=1;i=6156 | CanInterface | Object | CAN bus / SAE J1939 diagnostic interface of the engine ECU. |
| ns=1;i=6157 | Aftertreatment | Object | Exhaust aftertreatment subsystem, when equipped. |
| ns=1;i=1004 | AlternatorPhaseType | ObjectType | Per-phase electrical measurements of the alternator output. |
| ns=1;i=6158 | LineToNeutralVoltage | Variable | Phase (line-to-neutral) RMS voltage. EngineeringUnits: V. |
| ns=1;i=6159 | EngineeringUnits | Variable |  |
| ns=1;i=6160 | LineToLineVoltage | Variable | Line-to-line RMS voltage referenced to the next phase. EngineeringUnits: V. |
| ns=1;i=6161 | EngineeringUnits | Variable |  |
| ns=1;i=6162 | Current | Variable | Phase RMS current. EngineeringUnits: A. |
| ns=1;i=6163 | EngineeringUnits | Variable |  |
| ns=1;i=6164 | RealPower | Variable | Per-phase real power. EngineeringUnits: kW. |
| ns=1;i=6165 | EngineeringUnits | Variable |  |
| ns=1;i=6166 | ReactivePower | Variable | Per-phase reactive power. EngineeringUnits: kvar. |
| ns=1;i=6167 | EngineeringUnits | Variable |  |
| ns=1;i=6168 | ApparentPower | Variable | Per-phase apparent power. EngineeringUnits: kVA. |
| ns=1;i=6169 | EngineeringUnits | Variable |  |
| ns=1;i=6170 | PowerFactor | Variable | Per-phase power factor (-1..1). |
| ns=1;i=1003 | AlternatorType | ObjectType | The alternator (generator end) that converts mechanical power into AC electrical power. Exposes aggregate and per-phase electrical measurements. |
| ns=1;i=6171 | Frequency | Variable | Output frequency. EngineeringUnits: Hz. |
| ns=1;i=6172 | EngineeringUnits | Variable |  |
| ns=1;i=6173 | AverageLineToLineVoltage | Variable | Average line-to-line RMS voltage. EngineeringUnits: V. |
| ns=1;i=6174 | EngineeringUnits | Variable |  |
| ns=1;i=6175 | AverageLineToNeutralVoltage | Variable | Average line-to-neutral RMS voltage. EngineeringUnits: V. |
| ns=1;i=6176 | EngineeringUnits | Variable |  |
| ns=1;i=6177 | AverageCurrent | Variable | Average line RMS current. EngineeringUnits: A. |
| ns=1;i=6178 | EngineeringUnits | Variable |  |
| ns=1;i=6179 | TotalRealPower | Variable | Total three-phase real power. EngineeringUnits: kW. |
| ns=1;i=6180 | EngineeringUnits | Variable |  |
| ns=1;i=6181 | TotalReactivePower | Variable | Total three-phase reactive power. EngineeringUnits: kvar. |
| ns=1;i=6182 | EngineeringUnits | Variable |  |
| ns=1;i=6183 | TotalApparentPower | Variable | Total three-phase apparent power. EngineeringUnits: kVA. |
| ns=1;i=6184 | EngineeringUnits | Variable |  |
| ns=1;i=6185 | AveragePowerFactor | Variable | Average power factor (-1..1). |
| ns=1;i=6186 | TotalRealEnergy | Variable | Cumulative generated real energy. EngineeringUnits: kW.h. |
| ns=1;i=6187 | EngineeringUnits | Variable |  |
| ns=1;i=6188 | LoadPercent | Variable | Output as a percentage of rated power. EngineeringUnits: %. |
| ns=1;i=6189 | EngineeringUnits | Variable |  |
| ns=1;i=6190 | WindingTemperature1 | Variable | Stator winding temperature, phase 1. EngineeringUnits: degC. |
| ns=1;i=6191 | EngineeringUnits | Variable |  |
| ns=1;i=6192 | WindingTemperature2 | Variable | Stator winding temperature, phase 2. EngineeringUnits: degC. |
| ns=1;i=6193 | EngineeringUnits | Variable |  |
| ns=1;i=6194 | WindingTemperature3 | Variable | Stator winding temperature, phase 3. EngineeringUnits: degC. |
| ns=1;i=6195 | EngineeringUnits | Variable |  |
| ns=1;i=6196 | BearingTemperatureDriveEnd | Variable | Drive-end bearing temperature. EngineeringUnits: degC. |
| ns=1;i=6197 | EngineeringUnits | Variable |  |
| ns=1;i=6198 | BearingTemperatureNonDriveEnd | Variable | Non-drive-end bearing temperature. EngineeringUnits: degC. |
| ns=1;i=6199 | EngineeringUnits | Variable |  |
| ns=1;i=6200 | Connection | Variable | Winding connection configuration. |
| ns=1;i=6201 | ExcitationType | Variable | Excitation method. |
| ns=1;i=6202 | NumberOfPoles | Variable | Number of alternator poles. |
| ns=1;i=6203 | VoltageSetpoint | Variable | AVR voltage setpoint. EngineeringUnits: V. |
| ns=1;i=6204 | EngineeringUnits | Variable |  |
| ns=1;i=6205 | FieldCurrent | Variable | Excitation field current. EngineeringUnits: A. |
| ns=1;i=6206 | EngineeringUnits | Variable |  |
| ns=1;i=6207 | L1 | Object | Phase 1 (A) measurements. |
| ns=1;i=6208 | L2 | Object | Phase 2 (B) measurements. |
| ns=1;i=6209 | L3 | Object | Phase 3 (C) measurements. |
| ns=1;i=1005 | FuelSystemType | ObjectType | The fuel storage and delivery subsystem of a generator set. |
| ns=1;i=6210 | FuelType | Variable | Primary fuel of the set. |
| ns=1;i=6211 | FuelLevel | Variable | Fuel tank level. EngineeringUnits: %. |
| ns=1;i=6212 | EngineeringUnits | Variable |  |
| ns=1;i=6213 | FuelVolume | Variable | Usable fuel volume remaining. EngineeringUnits: l. |
| ns=1;i=6214 | EngineeringUnits | Variable |  |
| ns=1;i=6215 | FuelConsumptionRate | Variable | Fuel consumption rate. EngineeringUnits: L/h. |
| ns=1;i=6216 | EngineeringUnits | Variable |  |
| ns=1;i=6217 | FuelPressure | Variable | Fuel supply pressure. EngineeringUnits: kPa. |
| ns=1;i=6218 | EngineeringUnits | Variable |  |
| ns=1;i=6219 | FuelTemperature | Variable | Fuel temperature. EngineeringUnits: degC. |
| ns=1;i=6220 | EngineeringUnits | Variable |  |
| ns=1;i=6221 | GasSupplyPressure | Variable | Gas inlet pressure for gaseous-fuel sets. EngineeringUnits: kPa. |
| ns=1;i=6222 | EngineeringUnits | Variable |  |
| ns=1;i=6223 | RuntimeRemaining | Variable | Estimated runtime remaining at current load. EngineeringUnits: h. |
| ns=1;i=6224 | EngineeringUnits | Variable |  |
| ns=1;i=6225 | TotalFuelConsumed | Variable | Cumulative fuel consumed. EngineeringUnits: l. |
| ns=1;i=6226 | EngineeringUnits | Variable |  |
| ns=1;i=6227 | WaterInFuel | Variable | Water detected in the fuel/water separator. |
| ns=1;i=1006 | CoolingSystemType | ObjectType | The engine cooling subsystem of a generator set. |
| ns=1;i=6228 | CoolantTemperature | Variable | Engine coolant temperature. EngineeringUnits: degC. |
| ns=1;i=6229 | EngineeringUnits | Variable |  |
| ns=1;i=6230 | CoolantLevel | Variable | Coolant level. SAE J1939 SPN 111. EngineeringUnits: %. |
| ns=1;i=6231 | EngineeringUnits | Variable |  |
| ns=1;i=6232 | CoolantPressure | Variable | Coolant pressure. EngineeringUnits: kPa. |
| ns=1;i=6233 | EngineeringUnits | Variable |  |
| ns=1;i=6234 | CoolingMethod | Variable | Cooling method (air- or liquid-cooled). |
| ns=1;i=6235 | AmbientTemperature | Variable | Ambient air temperature at the set. EngineeringUnits: degC. |
| ns=1;i=6236 | EngineeringUnits | Variable |  |
| ns=1;i=6237 | RadiatorFanRunning | Variable | The radiator fan is running. |
| ns=1;i=6238 | JacketWaterHeaterActive | Variable | The jacket-water block heater is active. |
| ns=1;i=1007 | LubricationSystemType | ObjectType | The engine lubrication subsystem of a generator set. |
| ns=1;i=6239 | OilPressure | Variable | Engine oil pressure. SAE J1939 SPN 100. EngineeringUnits: kPa. |
| ns=1;i=6240 | EngineeringUnits | Variable |  |
| ns=1;i=6241 | OilTemperature | Variable | Engine oil temperature. SAE J1939 SPN 175. EngineeringUnits: degC. |
| ns=1;i=6242 | EngineeringUnits | Variable |  |
| ns=1;i=6243 | OilLevel | Variable | Engine oil level. EngineeringUnits: %. |
| ns=1;i=6244 | EngineeringUnits | Variable |  |
| ns=1;i=6245 | OilFilterDifferentialPressure | Variable | Oil filter differential pressure. EngineeringUnits: kPa. |
| ns=1;i=6246 | EngineeringUnits | Variable |  |
| ns=1;i=1008 | StartingSystemType | ObjectType | The starting/battery subsystem of a generator set. |
| ns=1;i=6247 | BatteryVoltage | Variable | Starting battery voltage. SAE J1939 SPN 168. EngineeringUnits: V. |
| ns=1;i=6248 | EngineeringUnits | Variable |  |
| ns=1;i=6249 | BatteryChargingCurrent | Variable | Battery charging current. EngineeringUnits: A. |
| ns=1;i=6250 | EngineeringUnits | Variable |  |
| ns=1;i=6251 | BatteryChargerActive | Variable | The battery charger is active. |
| ns=1;i=6252 | StartAttempts | Variable | Number of start attempts in the last start sequence. |
| ns=1;i=1009 | GeneratorControllerType | ObjectType | The generator set control panel. Provides controller identity, mode/state visibility and remote-monitoring status. |
| ns=1;i=6253 | ControllerFamily | Variable | Vendor controller product family or product line. |
| ns=1;i=6254 | FirmwareVersion | Variable | Controller firmware version. |
| ns=1;i=6255 | ApplicationSoftwareVersion | Variable | Application software version. |
| ns=1;i=6256 | ConfigurationVersion | Variable | Configuration/calibration version. |
| ns=1;i=6257 | InAutoMode | Variable | The controller is in automatic mode. |
| ns=1;i=6258 | NotInAuto | Variable | The controller is NOT in automatic mode (NFPA annunciation). |
| ns=1;i=6259 | RemoteStartEnabled | Variable | Remote start is enabled. |
| ns=1;i=6260 | RemoteControlEnabled | Variable | Remote control is enabled. |
| ns=1;i=6261 | CloudConnected | Variable | Connected to the remote-monitoring cloud. |
| ns=1;i=6262 | ModbusEnabled | Variable | The Modbus interface is enabled. |
| ns=1;i=6263 | SignalStrength | Variable | Cellular/network signal strength. EngineeringUnits: %. |
| ns=1;i=6264 | EngineeringUnits | Variable |  |
| ns=1;i=1012 | GeneratorRatingType | ObjectType | A single nameplate power rating point of a generator set for a given application/duty (ISO 8528). |
| ns=1;i=6265 | ApplicationRating | Variable | Application/duty of this rating. |
| ns=1;i=6266 | RatedRealPower | Variable | Rated real power. EngineeringUnits: kW. |
| ns=1;i=6267 | EngineeringUnits | Variable |  |
| ns=1;i=6268 | RatedApparentPower | Variable | Rated apparent power. EngineeringUnits: kVA. |
| ns=1;i=6269 | EngineeringUnits | Variable |  |
| ns=1;i=6270 | RatedPowerFactor | Variable | Rated power factor. |
| ns=1;i=6271 | RatedVoltage | Variable | Rated line-to-line voltage. EngineeringUnits: V. |
| ns=1;i=6272 | EngineeringUnits | Variable |  |
| ns=1;i=6273 | RatedCurrent | Variable | Rated line current. EngineeringUnits: A. |
| ns=1;i=6274 | EngineeringUnits | Variable |  |
| ns=1;i=6275 | RatedFrequency | Variable | Rated frequency. EngineeringUnits: Hz. |
| ns=1;i=6276 | EngineeringUnits | Variable |  |
| ns=1;i=6277 | RatedSpeed | Variable | Rated engine speed. EngineeringUnits: rpm. |
| ns=1;i=6278 | EngineeringUnits | Variable |  |
| ns=1;i=6279 | PhaseCount | Variable | Number of phases (1 or 3). |
| ns=1;i=6280 | Connection | Variable | Winding connection for this rating. |
| ns=1;i=6281 | AmbientTemperature | Variable | Reference ambient temperature for the rating. EngineeringUnits: degC. |
| ns=1;i=6282 | EngineeringUnits | Variable |  |
| ns=1;i=6283 | Altitude | Variable | Reference altitude for the rating. EngineeringUnits: m. |
| ns=1;i=6284 | EngineeringUnits | Variable |  |
| ns=1;i=1017 | GeneratorProtectionAlarmType | ObjectType | Alarm raised by a generator protection/shutdown function. Extends OffNormalAlarmType with the protection function, automatic protection action and J1939 origin. The inherited Severity field is the sole event urgency. |
| ns=1;i=6285 | ProtectionFunction | Variable | The protection function that raised the alarm. |
| ns=1;i=6286 | GeneratorAlarmSeverity | Variable | Severity class of the alarm. |
| ns=1;i=6287 | IsShutdown | Variable | TRUE if the engine is actually shut down. This reports the outcome and is not inferred from ProtectionAction. |
| ns=1;i=6288 | Spn | Variable | SAE J1939 SPN when the alarm originates from the engine ECU. |
| ns=1;i=6289 | Fmi | Variable | SAE J1939 FMI when the alarm originates from the engine ECU. |
| ns=1;i=6290 | SubsystemName | Variable | Name of the originating subsystem. |
| ns=1;i=1001 | GeneratorSetType | ObjectType | A generator set (GenSet): a complete electrical power generation asset composed of a prime-mover engine, an alternator, a fuel system, cooling, lubrication, starting and control subsystems. Applicable to the whole industry, from small home-standby units to house-sized multi-megawatt industrial sets. |
| ns=1;i=6291 | Identification | Object | Generator identification and nameplate (Machinery building block). |
| ns=1;i=6292 | MachineryBuildingBlocks | Object | Container for standardized Machinery building blocks. |
| ns=1;i=6293 | MachineryItemState | Object | Generic Machinery availability state machine (interoperability). |
| ns=1;i=6294 | MachineryOperationMode | Object | Derived Machinery operation-mode state machine for interoperability. OperatingMode is authoritative and the specification defines the deterministic mapping to this state machine. |
| ns=1;i=6295 | OperatingState | Object | Detailed generator-set operating state machine. |
| ns=1;i=6296 | OperatingMode | Variable | Authoritative selector mode of the control panel (Off/Manual/Auto/Test/...). Where MachineryOperationMode is present, its CurrentState is derived from this value. |
| ns=1;i=6297 | EmissionsStandard | Variable | Emissions certification standard of the set. |
| ns=1;i=6298 | Application | Variable | Application segment, e.g. Residential, DataCenter, Healthcare, Rental, PrimePower. |
| ns=1;i=6299 | GeneratorBreakerClosed | Variable | The generator (output) breaker is closed. |
| ns=1;i=6300 | GeneratorBreakerAvailable | Variable | The generator breaker is available to close. |
| ns=1;i=6301 | RemoteStartInput | Variable | The remote start input is asserted. |
| ns=1;i=6302 | RunRequest | Variable | A run request is active from any source. |
| ns=1;i=6303 | LoadInhibit | Variable | Loading of the set is inhibited. |
| ns=1;i=6304 | AvailableToLoad | Variable | The set is up to speed and voltage and is ready to accept load. |
| ns=1;i=6305 | Engine | Object | The prime-mover engine. |
| ns=1;i=6306 | Alternator | Object | The alternator (generator end). |
| ns=1;i=6307 | Controller | Object | The control panel. |
| ns=1;i=6308 | FuelSystem | Object | The fuel subsystem. |
| ns=1;i=6309 | CoolingSystem | Object | The cooling subsystem. |
| ns=1;i=6310 | LubricationSystem | Object | The lubrication subsystem. |
| ns=1;i=6311 | StartingSystem | Object | The starting/battery subsystem. |
| ns=1;i=6312 | Ratings | Object | Nameplate power ratings of the set (e.g. Standby and Prime). |
| ns=1;i=6313 | <Rating> | Object | A nameplate rating point of the set. |
| ns=1;i=6314 | Start | Method | Command the set to start in the current operating mode. |
| ns=1;i=6315 | Stop | Method | Command a normal stop (with cooldown). |
| ns=1;i=6316 | EmergencyStop | Method | Command an immediate emergency stop. |
| ns=1;i=6317 | ResetFaults | Method | Reset latched faults / lockout. |
| ns=1;i=6318 | SetOperatingMode | Method | Set the control-panel selector mode. |
| ns=1;i=6319 | InputArguments | Variable |  |
| ns=1;i=6320 | StartTest | Method | Start a test run for a given duration. |
| ns=1;i=6321 | InputArguments | Variable |  |
| ns=1;i=1019 | TransferSwitchSourceType | ObjectType | One power source (normal/utility or emergency/generator) of an automatic transfer switch, with its availability and measurements. |
| ns=1;i=6322 | Available | Variable | The source is present and energized. |
| ns=1;i=6323 | Acceptable | Variable | The source is within acceptable voltage/frequency limits. |
| ns=1;i=6324 | Voltage | Variable | Source line-to-line voltage. EngineeringUnits: V. |
| ns=1;i=6325 | EngineeringUnits | Variable |  |
| ns=1;i=6326 | Frequency | Variable | Source frequency. EngineeringUnits: Hz. |
| ns=1;i=6327 | EngineeringUnits | Variable |  |
| ns=1;i=6328 | PhaseRotation | Variable | Phase rotation of the source (e.g. ABC or CBA). |
| ns=1;i=1013 | AutomaticTransferSwitchType | ObjectType | An automatic transfer switch (ATS) that transfers a load between a normal source (utility) and an emergency source (generator). |
| ns=1;i=6329 | Identification | Object | ATS identification and nameplate. |
| ns=1;i=6330 | Position | Variable | Contact position of the switch. |
| ns=1;i=6331 | OperatingState | Variable | Operating state of the switch. |
| ns=1;i=6332 | TransitionType | Variable | Transition method of the switch. |
| ns=1;i=6333 | Source1 | Object | Source 1 (normal/utility). |
| ns=1;i=6334 | Source2 | Object | Source 2 (emergency/generator). |
| ns=1;i=6335 | PreferredSource | Variable | The preferred source (1 = normal, 2 = emergency). |
| ns=1;i=6336 | Source1Connected | Variable | The load is connected to Source 1. |
| ns=1;i=6337 | Source2Connected | Variable | The load is connected to Source 2. |
| ns=1;i=6338 | TransferInhibited | Variable | Transfer is currently inhibited. |
| ns=1;i=6339 | TransferInhibitReason | Variable | Reason transfer is inhibited, if any. |
| ns=1;i=6340 | RatedCurrent | Variable | Rated current of the switch. EngineeringUnits: A. |
| ns=1;i=6341 | EngineeringUnits | Variable |  |
| ns=1;i=6342 | PoleCount | Variable | Number of poles. |
| ns=1;i=6343 | ServiceEntranceRated | Variable | The switch is service-entrance rated. |
| ns=1;i=6344 | LoadCurrent | Variable | Load current through the switch. EngineeringUnits: A. |
| ns=1;i=6345 | EngineeringUnits | Variable |  |
| ns=1;i=6346 | TransferCount | Variable | Cumulative number of transfers. |
| ns=1;i=6347 | LastTransferTime | Variable | Timestamp of the last transfer. |
| ns=1;i=6348 | EngineStartDelay | Variable | Engine-start (outage confirmation) delay. |
| ns=1;i=6349 | TransferToEmergencyDelay | Variable | Delay before transferring to emergency. |
| ns=1;i=6350 | RetransferToNormalDelay | Variable | Delay before retransferring to normal. |
| ns=1;i=6351 | CooldownDelay | Variable | Engine cooldown (unloaded run) delay. |
| ns=1;i=6352 | Transfer | Method | Command a transfer to the emergency source. |
| ns=1;i=6353 | Retransfer | Method | Command a retransfer to the normal source. |
| ns=1;i=6354 | InhibitTransfer | Method | Enable or disable the transfer inhibit. |
| ns=1;i=6355 | InputArguments | Variable |  |
| ns=1;i=1014 | ParallelingControllerType | ObjectType | A paralleling / switchgear controller that synchronizes and shares load among generator sets on a common bus, and optionally parallels with the utility. |
| ns=1;i=6356 | SystemState | Variable | Operating state of the paralleling system. |
| ns=1;i=6357 | BusVoltage | Variable | Common bus voltage. EngineeringUnits: V. |
| ns=1;i=6358 | EngineeringUnits | Variable |  |
| ns=1;i=6359 | BusFrequency | Variable | Common bus frequency. EngineeringUnits: Hz. |
| ns=1;i=6360 | EngineeringUnits | Variable |  |
| ns=1;i=6361 | TotalBusRealPower | Variable | Total real power on the bus. EngineeringUnits: kW. |
| ns=1;i=6362 | EngineeringUnits | Variable |  |
| ns=1;i=6363 | TotalBusReactivePower | Variable | Total reactive power on the bus. EngineeringUnits: kvar. |
| ns=1;i=6364 | EngineeringUnits | Variable |  |
| ns=1;i=6365 | SynchronizationAngle | Variable | Phase angle difference during synchronizing. EngineeringUnits: deg. |
| ns=1;i=6366 | EngineeringUnits | Variable |  |
| ns=1;i=6367 | SlipFrequency | Variable | Slip frequency during synchronizing. EngineeringUnits: Hz. |
| ns=1;i=6368 | EngineeringUnits | Variable |  |
| ns=1;i=6369 | VoltageDifference | Variable | Voltage difference during synchronizing. EngineeringUnits: V. |
| ns=1;i=6370 | EngineeringUnits | Variable |  |
| ns=1;i=6371 | FrequencyDifference | Variable | Frequency difference during synchronizing. EngineeringUnits: Hz. |
| ns=1;i=6372 | EngineeringUnits | Variable |  |
| ns=1;i=6373 | SyncCheckPermissive | Variable | Synchronism-check permissive to close. |
| ns=1;i=6374 | DeadBus | Variable | The bus is dead (de-energized). |
| ns=1;i=6375 | LoadSharePercent | Variable | This set's share of the total bus load. EngineeringUnits: %. |
| ns=1;i=6376 | EngineeringUnits | Variable |  |
| ns=1;i=6377 | AvailableCapacity | Variable | Available spare capacity on the bus. EngineeringUnits: kW. |
| ns=1;i=6378 | EngineeringUnits | Variable |  |
| ns=1;i=6379 | SpinningReserve | Variable | Spinning reserve on the bus. EngineeringUnits: kW. |
| ns=1;i=6380 | EngineeringUnits | Variable |  |
| ns=1;i=6381 | GeneratorBreakerClosed | Variable | The generator breaker is closed. |
| ns=1;i=6382 | UtilityBreakerClosed | Variable | The utility breaker is closed. |
| ns=1;i=6383 | UtilityImportPower | Variable | Power imported from the utility. EngineeringUnits: kW. |
| ns=1;i=6384 | EngineeringUnits | Variable |  |
| ns=1;i=6385 | UtilityExportPower | Variable | Power exported to the utility. EngineeringUnits: kW. |
| ns=1;i=6386 | EngineeringUnits | Variable |  |
| ns=1;i=6387 | ConnectToBus | Method | Synchronize and close onto the common bus. |
| ns=1;i=6388 | DisconnectFromBus | Method | Soft-unload and open from the common bus. |
| ns=1;i=1015 | GeneratorSystemType | ObjectType | A power-generation system aggregating one or more paralleled generator sets, an optional paralleling controller and transfer switches. Models integrated power systems such as data-center and healthcare plants. |
| ns=1;i=6389 | GeneratorSets | Object | The generator sets that make up the system. |
| ns=1;i=6390 | <GeneratorSet> | Object | A generator set participating in the system. |
| ns=1;i=6391 | ParallelingController | Object | The paralleling/switchgear controller of the system. |
| ns=1;i=6392 | TransferSwitches | Object | The transfer switches in the system. |
| ns=1;i=6393 | <TransferSwitch> | Object | A transfer switch in the system. |
| ns=1;i=6394 | NumberOfGeneratorSets | Variable | Number of generator sets in the system. |
| ns=1;i=6395 | TotalSystemCapacity | Variable | Total installed capacity of the system. EngineeringUnits: kW. |
| ns=1;i=6396 | EngineeringUnits | Variable |  |
| ns=1;i=6397 | TotalSystemLoad | Variable | Total load currently served by the system. EngineeringUnits: kW. |
| ns=1;i=6398 | EngineeringUnits | Variable |  |
| ns=1;i=6399 | RedundancyScheme | Variable | Redundancy scheme, e.g. N, N+1, N+2, 2N, DistributedRedundant. |
| ns=1;i=3018 | GeneratorProtectionActionEnum | DataType | Automatic response requested by a generator protection function. This is independent of the standard Part 9 event Severity. |
| ns=1;i=3918 | EnumStrings | Variable |  |
| ns=1;i=3051 | DiagnosticTroubleCodeDataType | DataType | A SAE J1939 diagnostic trouble code (DTC) reported by an engine ECU. |
| ns=1;i=6400 | Default Binary | Object |  |
| ns=1;i=6401 | Default XML | Object |  |
| ns=1;i=6402 | ActiveDiagnosticTroubleCodeDetails | Variable | Currently active DTCs (J1939 DM1) using the current DataType. |
| ns=1;i=6403 | PreviouslyActiveDiagnosticTroubleCodeDetails | Variable | Previously active DTCs (J1939 DM2) using the current DataType. |
| ns=1;i=6404 | ProtectionAction | Variable | Automatic response requested by the protection function. This classification does not replace or determine the inherited Part 9 Severity. |

_____________

—————————